## Comments
Field |  | Review Comment Type | [5 empty] | Action
Software |  | Q | Open Question/Missing Information
Mechanical |  | U | Understanding/Unclear Formulation
Electronics: cabling, connectors |  | M | Mistake
Procedure |  | I | Internal Comment
Safety |  | R | Request for change
Documentation |  | S | Suggestions for improvements
Field | ID | Type | Page | Ref | Comment | Reviewer | Date | Status | Answer to Comment / Proposed Action
Electronics | 1 | R |  |  | BNC connector on front of CC is unlabelled (Bdot) | Heine | 2017-12-15 | Remove from design | Signal is not used by supplies
Electronics | 2 | Q |  |  | Consider location of Bdot signal connector on CC: rear or front | Heine | 2017-12-15 | Remove from design | Signal is not used by supplies
Electronics | 3 | R |  |  | Propose a solution for CC, where IPC is integrated into chassis such that less rack height is consumed by this unit | Heine | 2017-12-15 | Accepted by DF
Electronics | 4 | R |  |  | Add screws to secure all cables, e.g. ribbon cables | Heine | 2017-12-15 | Accepted by DF
Software | 5 | S |  |  | Please consider to let each supply have a unique serial number that can be read from the supply. Ideally this would be the response from a separate request, but to include it in the IDN? Response would also work. This ensures that the operator is communicating with the "right" supply. As it is now, they appear indistinguishable on the network (apart from MAC address) | Heine | 2017-12-15 | Will not be included
Software | 6 | S |  |  | Since the raster frequency is an essential parameter in the operation of the supply, it would be preferable to have this parameter visible in the main display of each supply | Heine | 2017-12-15 | Will not be included
Electronics | 7 | Q |  |  | Would it be possible to have measurement of the fan revolution speeds that could be read out from CC? | Stephane Gabourin | 2017-12-19 | Will not be included
Electronics | 8 | Q |  |  | Pol missing (ISO15): could this be changed to deliver the supply's interpretation of the polarity sync signal? It does not seem to include hardware changes. Currently ISO15 represents whether the polarity sync signal was recognized or not; not what it recognized it to be | Stephane Gabourin | 2017-12-19 | Considered by DF | A matter of revising VHDL code. It may require consultancy hours
Procedure | 9 | R |  |  | Please perform thermal imaging of components inside terminal boxes during maximum system performance during FAT to verify that all components are mounted and cooled according to the design | Heine | 2018-01-09 | Accepted by DF | Will be included in FAT-II
Mechanical | 10 | R |  |  | Reconsider cooling of terminal box: water cooling is approved by ESS and cooling loop parameters have been provided | Iñigo Alonso | 2018-01-09 | Accepted by DF
Mechanical | 11 | R |  |  | Please make one or several openings at the bottom of the girder stands of sizes similar to the ones at the top of the stands. This allows feasible retrieval of items lost in the stands (tools etc.) | Iñigo Alonso | 2018-01-09 | Accepted by DF
Elctronics | 12 | Q |  |  | Have the necessity of snubber circuits across the MOSFETs been considered, having both voltage waveform quality and component lifetime in mind? Are such compensating circuits already implemented in the design? | Heine | 2018-01-12 | Closed. Found to be unnecessary | MOSFETs are decoupled via DC-link capacitor PCB (low stray inductance, laminated/sandwich construction). Voltage measurements during design validation confirmed very limited voltage transients during switching - far within the voltage rating of the semiconductors. 60 V overshoot was measured with full current and 600 V on the DC-link. The MOSFETs are rated for a V_DS of 1200 V
Electronics | 13 | Q |  |  | Could the signal from the integrated current transducers be made available through a BNC connector on the chassis without disturbing the regulation loops etc.? | Søren Pape Møller | 2018-01-12 | Would require substantial redesign. | Simpler to use dedicated current transformer
Mechanical | 14 | R |  |  | Reduce busbar cover openings: it seems one could reach the top magnet coil terminal and perhaps also the cable-to-busbar connection using a finger | Heine | 2018-03-14 | Accepted by DF
Mechanical | 15 | R |  |  | Consider a non-conductive, and possibly transparent, material for the busbar covers | Inigo | 2018-03-15 | No change to design: use metallic covers as on pre-series | Plastic covers are expected to deteriorate in the A2T radiation field. The busbars are insulated with a woven glass fabric, the busbars are fixed to the coils (fixed to magnet housing) and G11 brackets on girder. Coil terminals and cable ends are fixed accordingly.
Mechanical | 16 | R |  |  | Please consider covers on the back of the OC to cover the connections of the power cables | Heine | 2018-03-14
Mechanical | 17 | R |  |  | Ensure that flange orientation has the channel for He-leak testing orientated upwards | Fabio | 2018-03-15
Mechanical | 18 | R |  |  | The G11 bracket that fixates the individual conductors just below the connection to the busbars should be redesigned with a larger opening or longer bolts, as the bracket could not be mounted as delivered | Heine | 2018-03-16 | Accepted by DF | Longer bolts will be used
Mechanical | 19 | R |  |  | Please provide better access to the two transverse turnbuckle alignment fixtures of the girder, i.e. Ensure that there is sufficient clearance to use a spanner for adjustments | Fabio | 2018-03-16 | Closed. Found to be unnecessary | Existing design should be acceptable when girder is placed in nominal beam height. Pre-series is put about 40 mm lower than nominal beam height, thus leaving less room for adjustments
Procedure | 20 | S |  |  | Please keep an attention on magnet coil polarity during production steps | Heine | 2018-03-16 | Accepted by DF | Replacement test coil was unintentionally bent into a mirrored saddle shape (before attaching terminals), thus giving an opposite current direction and polarity
Mechanical | 21 | S |  |  | Consider that the two termination boxes related to the same girder will need to be mirrored to some extent: they are facing each other but will e.g. have to be accessed from the same side of the tunnel | Iñigo Alonso | 2018-04-06 | Accepted by DF
Procedure / documentation | 22 | Q |  |  | Please provide a FAT programme description for the production series | Heine | 2018-04-17 |  | The production series FAT programme will be input for the CDR-3