## Sheet1
Measurements performed during FAT at Danfysik, 2017.11.29
Stray field measured with ~1 cm^2 pickup coil, single winding
| Position from center | Peak voltage
| mm | mV
| 0 | 291
| 140 | 143
| 200 | 32
| 400 | 0.74
Quick-CF clamp was placed ~20 mm from magnet coil edge. System was operated at 340 A, 40 kHz, 14 Hz for about 30 min. No significant heating of the clamp was found
| Polarity sync frequency acceptance | Unit | Nominal | Min | Max
| Frequency accepted | kHz | 10 | 5 | 129
| Duty cycle | % | 50 | 40 | 60
Synchronization of supplies
| Method | The temporal location of the final zero-crossing of the burst relative to a trigger set on the pre-trigger
| Result | The suppllies are found to be synchronized within 40 ns