## Slide 1: Chopper control update 7th ECP workshop
Markus Olsson
Control system engineer
www.europeanspallationsource.se
3 September, 2018

## Slide 2: Choppers
Rotating discs 700-1400mm 14-350Hz
100 choppers in 15 instruments
About 40 chopper racks

## Slide 3: Chopper control concept
Engineering HMI
(CS-Studio)
Synchronization signal (7-406Hz)
EPICS
CHIC Standard Comm. template
CHIC
Control Interface
Chopper MPS
Diagnostics
Monitoring
Chopper Package (1..N)
Motor & Bearing Control
Sensors
Ref input
Time stamping
(TDC pulse)
EPICS IOC
DMSC
User interface
Data analysis
Timing System
TDC output
SKF
Kollmorgen
Jülich
Other DCU
Software interface modules
CHIC IOC
Timing IOC

## Slide 4
Data logging
Message layers (ESS+Airbus)
Interlock
Outputs
Supplier 1
Supplier 2
Supplier n
Control interface
GUI
EPICS layer
Supplier 1
Supplier 2
Supplier n
Monitoring
Chopper Controller 1
External Sensors 1
Chopper Controller 2
External Sensors 2
Chopper Controller n
External Sensors 3
EPICS Layer
CHIC Layer
Chopper Layer

## Slide 5
Data Base
All data from the CHIC and timing system is stored in a data base and/or sent to DMSC
Configuration data base (CCDB) (PLC config files)
CHIC PVs
Control
Alarms
Status
Sensor data
FFT Vibration monitoring
Monitoring system
Real time diagnostics
Condition monitoring
GUI
EPICS Layer
CHIC Layer
Interface to CHIC
Timing PVs
Frequencies
Phase delays
TDC pulses
Reference pulses
DMSCLayer
DMSC Chopper user interface

## Slide 6: EPICS – Beckhoff interface overview
EPICS
ESS Message layer
(In ST)
Modbus TCP/IP
TCP/IP
Airbus Message layer (C++)
TcCOM
CHIC Beckhoff
Modbus TCP/IP to PLC
TCP/IP to EPICS
Two ”message layers” one in ST (owned by ESS) one in C++ owned by Airbus.
Full implementation of all layers scheduled to fall 2018.

## Slide 7: Automated script – PLC Factory
EPICS IOC
PLC
PLC Factory
(python script)
ST code
EPICS
module
Config file
Variables for control and monitoring
Developed by Miklós Boros and Andrés Quintanilla
Variables for control and monitoring.
The script will create two sets of code, one to PLC and one to an EPICS module
Will save a lot of time and reduce the risk of human errors.

## Slide 8: Automated script – PLC Factory
PLC Factory
(python script)
ST code
EPICS
module
Config file
Variables for control and monitoring
Developed by Miklós Boros and Andrés Quintanilla
Variables for control and monitoring.
The script will create two sets of code, one to PLC and one to an EPICS module
Will save a lot of time and reduce the risk of human errors.
PLC
EPICS

## Slide 9: Hardware design
Crate 4U or 6U
PLC (Beckhoff)
VSE100 (Vibration Monitoring)
2 x Power supply
Remote controlled Switch
Analog I/Os
Digital I/Os
Fieldbuses (Ethernet ports)
External hard drive

## Slide 10: CHIC prototype
First prototype crate made by Airbus spring 2018
Second prototype in design stage. To be built fall 2018.
Third version delivered spring 2019

## Slide 11: Chopper control rack
Variant of the ESS standard instrument rack
  Designed according to ESS standards and SE legislation.
The rack is discussed together with suppliers
Part of the control system in-kind with Jülich.
Prototype delivered spring 2019
Prototype chopper control rack

## Slide 12: Verification and validation
New 300 MHz oscilloscope for verification of timing and chopper accuracy
Jitter and chopper phase error can be plotted directly in a histogram with 2 ns resolution
Possible to connect accelerometers for additional vibration analysis.

## Slide 13: Timing update
Frequencies 14-350Hz generated with the EVR
Two EVRs connected to one EVG
  Tested at utgård August 2018.
  440 ps jitter, resolution limited by our oscilloscope
440 ps

## Slide 14: Planned tests - fall 2018
Atomic clock ordered to improve time stamping in the EVR (for test purposes)
Test with laser to determine the angular offset between the TDC and a specific window in the disk.
Test timing system with high speed chopper (pre FAT)

## Slide 15: Chopper control timeline 2018/2019
2018
2019
Sept
Oct
Nov
Dec
Jan
Feb
Mar
Apr
May
June
July
75 days
2 days
Timing test on Airbus chopper?
55 days
CHIC integrated in EPICS
CDR CHIC
2019
Rack delivered
CHIC delivered
CHIC Software ready
for tests
Today
CHIC ready for deployment
FAT
Aug
SAT


## Slide 16: Rack locations
NMX, BEER
C-SPEC, BIFROST
MIRACLES, MAGIC
T-REX, HEIMDAL
LOKI, FREIA,
SLEIPNIR, NNBAR
ODIN, DREAM
VESPA
ANNI, SKADI
ESTIA?
ESTIA?

## Slide 17: Simple grounding rules
The chopper control rack shall always be in the same grounding zone as the chopper.
  Mixing grounding zones can cause damage on equipment or in worst case cause injuries.
A rack shall never be shared between instruments.
  To ensure the reliability of the instrument

## Slide 18: News
Finished critical design of the CHIC and the Control rack.

## Slide 19: Chopper timing
Markus Olsson
Control system engineer
www.europeanspallationsource.se
3 September, 2018

## Slide 20: ESS Timing
The 14 Hz operating frequency will be generated by down conversion from RF in the event generator (divide 88.0525 MHz by 6289464 to get 14.00000064 Hz)
All timing sequences, events, etc., generated in hardware
One or two event generators for NSS
Master Event Generator
RF Master Oscillator
fanout
Event
receiver
88 MHz
fanout
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver
Event
receiver

## Slide 21: Timing (Bifrost example)
Every rack will have an event receiver (EVR) that will provide ref frequencies to the choppers.
Frequencies from 3.5Hz to at least 406Hz will be created. (14Hz-350Hz tested)
Time stamp
Time stamp
Time stamp
Time stamp
Time stamp
Time stamp
EVR 14Hz
EVR 14Hz
14 Hz
14 Hz
210 Hz
210 Hz
14 Hz
14 Hz
EVG 88MHz

## Slide 22: Chopper timing
Different “pulse trains” are triggered by the rising edge of the 14 Hz event.

## Slide 23: Experiment 210Hz
JitTrack ctc jitter
Histogram ctc jitter

## Slide 24: Chopper timing
The maximum cycle to cycle jitter will be 11.3 ns for any frequency.
Every pulse can be adjusted back and forth in time with a resolution of 11,3 ns.
The jitter between the last pulse of the pulse train and the new 14 Hz pulse will not be more than 11.3 ns
Cycle to cycle jitter max 25 ns

## Slide 25: TDC offset determination
ɸ
Window edge
TDC
The TDC can be a magnet on the disc or a position on the shaft
The offset angle is predetermined with laser
Verified once when installed in beam

## Slide 26: Phase error and error propagation
Reference signal jitter: < 1ns precision
Chopper mechanical error: unknown but static at constant speed
TDC sensor error: unknown
Time stamping error: 11,3 ns precision
Determined with neutrons
Sent to DMSC

## Slide 27: Example of a timestamp
EPICS epoch since Jan 1st 1990
11,3 ns resolution
Absolute time us precision

## Slide 28: Chopper phase error
Talking directly to suppliers (Airbus, Jülich, SKF, Mirrotron)
Phase error = rising edge TDC – rising edge Ref
Can be measured easily with an oscilloscope (persistence on) for about 10 min.
Max phase error should be ±0.025° (± 5µs @ 14 Hz)

## Slide 29: Phase error experiment 14Hz

## Slide 30: Interface - Chopper Group/Instruments
What drives will be used? SKF communication module will be implemented into the CHIC fall 2018.
What communication protocol will be used between CHIC and drives. (Modbus preferred)
The drives can be used in “stand alone” mode during commissioning if needed.
Specific variables in the drive that will be monitored in the CHIC?