## Slide 1: Engineering Integration Utilities routing within the common shielding bunker
IKON 15
Talal Osman & Iain Sutton
www.europeanspallationsource.se
13 September, 2018

## Slide 2: Presentation overview
Scope
Progress
Solutions
Guidelines
Summary
Next steps

## Slide 3: Scope
Iain slide
Scope
Within shielding ‘bunker’ from Point of entry to Point of use
  Bunker entry
  Technical feed through
  Run
  Point of use connection
ENTRY
USE
USE
USE
4
3
2
1

## Slide 4: Objective
“Pave the way for the successful integration and installation of instrument systems into the bunker whilst ensuring personal safety and systems maintainability”
Deliverables
Routing strategy
  Meeting the needs of instrument and facility
Approved material list
  Fixtures & fittings
Engineering guidelines for implementation
  Decisions
  methods

## Slide 5: Utilities routing Progress
Needs
Electrical power
Signal
Vacuum
Cooling
PSS / MPS
Constrains
Access
Grounding
Fire
Radiation
Requirements
Concept
Solution development
Decision & Documentation
An illustration to explore parameter space and for discussion with stakeholders
Exploring options Evaluating solutions
Meeting needs & constraints
Making decisions Defining solutions
Getting agreement
IKON 14
IKON 15

## Slide 6: Solutions
Notes: What could possibly go wrong ?

## Slide 7: 1 Bunker entry (BR)Exit strategy
?
Solution is Very situation specific
Long instruments
  looks tractable
Short / Mid length
  looks tricky
More work required !
Grounding solution implemented here

## Slide 8: 2 Feed through
Section is adequate for all instruments
Built in ‘halfen’ rails for attachment
Good access for installation
Vacant space to be filled with bagged shielding as required.
  Steel shot
  Borated poly
New neutronics underway but no significant changes expected

## Slide 9: 3 Run
Standard feed through
Custom connection
Standard section (4/2/1)
Custom feeder
Chain Coupling
Rail
Compact
Support
Vertical
Cable
From feed through to POU it’s a Fixed installation
Route around access requirements
Exception for vacuum pipes (removable sections)

## Slide 10: 4 Point of Use going the last mile
R12 Quick Coupling
R12-R7 Feeder
Removable
Accessable
Q. Couplings
R7 > Chopper
Flexible / Snorkel
R12 > Rigid

## Slide 11: Engineering rules
All unities shall be exclusively supported by vertical support pillars or walls.
  No floor supports
All utilities shall enter the bunker through the roof level feed through.
  Except cooling services in the long sector shall enter at floor level through corner blocks
All utilities shall use the feed through located above their respective beam port.
  All exceptions must be formally approved by NSS management
Utilities shall follow the shortest route from point of entry to point of use
  Roof level routes shall be directly adjacent to vertical support pillars.
  Floor level routes shall run adjacent to walls …. then along the line of vertical support pillars
Utilities shall be routed to permit the removal of ‘Service components or RH components’ without their removal or displacement.
  Cable trays shall be routed around the extraction volume avoiding removal
  Fluids shall be routed around the extraction envelope, or if this results in unacceptable performance, removable sections shall be routed across the volume with the approval of RH.
All routing shall be positioned as far away from the neutron beam as practical.
  Roof level routes shall be positioned 25mm below the level of horizontal crossbeams.
  Floor level routes shall be positioned 50mm above floor plates
Utilities shall be packaged to minimizing their horizontal foot print
  Cable trays shall be orientated vertically and located directly adjacent to supports pillars
  Fluids shall be stacked vertically and positioned below cable trays

## Slide 12: Approved equipment list
n
MORE INFORMATION IN RH
DOCUMENT ESS-0042943
Cable trays / supports
  Wibe (schneider-electric)
Vacuum
  See vac group presentation
Cooling
  Pipe materials
Choppers
  Requirement Specs ESS-0059912

## Slide 13: Take away
Notes: What could possibly go wrong ?

## Slide 14: This mornings Take away
We believe we now have a workable strategy !
  > Workable routing for all instrument (we hope)
We have approved component suppliers
Implementation Guidelines
  For Own design or ESS design
Draft documents shortly on Confluence
https://confluence.esss.lu.se/x/wAs8Dw
Approved document will go on chess

## Slide 15: Next step
Completion of draft guideline – review - approval
Working on pricing structure and cost sharing for installation work.
Possibility of organizing activities together
  Same contactor
  Lower costs
  Simplified planning
Who interested ?

## Slide 16: Thank you for your attention !
NSS Projects Division
Instrument teams

## Slide 17: Extras

## Slide 18: Deployment a graded approach
n
0m
60cm
2.8cm
4cm
Moderator
200
170
140
81
20
10
8.6
7.1
4
1
100
86
71
44
10
MGy
MGy
kGy
Aluminum Gasket (> 20MGy)
Rad Hard EPDM O-ring (max. 20MGy)
Standard EPDM O-ring (max. 250kGy)
Requirement Specs ESS-0059912
6.05m
7m
8m
10m
12m
Neutron beam size 6x6cm

## Slide 19: Implementation
‘Back’
Full-RH or No-RH
‘Front’
Full-RH or Limited-RH
After 48-72hrs
Front access
  RH only
Rear access
  Hands on (hotspot removed)
After 10-15days
Front access
  RH only
  or Hands (hotspot removed)
Rear access
  Hands on
Restricted activities
Separation
Installation is not considered a RH-activity.
Notes: No in-situ RH maintenance is foreseen.
Installation is not considered a RH-activity.

## Slide 20: Scope
Instrument
  power & control
  Cooling
  Vacuum
  PSS / MPS
Bunker systems
  Power
  Lighting
  PSS
  Fluids