## Slide 1: LEBT water cooling system
Lars Rosberg
Senior Technician Cooling Water Systems
SRR 1 – Ion Source & LEBT
2018-07-17--18

## Slide 2: System – Cooling Water System
Plasma chamber
Extraction system
Pumping box
Solenoid
2 x steerer
Gate valve
Iris
Diagnostics tank
Gate valve
Solenoid
2 x steerer
Chopper
EMU H+V
Faraday cup
NPM H+V
Doppler shift
2 x TMP
Repeller
Repeller
ACCT
2 x TMP
Commissioning tank (RFQ)
2 x TMP
HV power supply
Isolation transformer
Collimator
Magnetron
H2 bottle
Ion source
LEBT 1
LEBT 2
3 x solenoid
Waveguide
Primary pump
Primary pump
High voltage (HV) platform
Ion source
Low energy beam transport (LEBT)
PSS0 controlled area
and radiation shielding
Front End and Magnets
Cooling water
Vacuum
PSS
Beam Diagnostics
Control system
ACCT
Voltage divider
EMU H+V
Faraday cup
NPM H+V
Doppler shift
HV controls
Ground potential controls
Beam stop
Alternative location of beam instruments for commissioning
N2 bottle
ACCT: AC current transformer
EMU: Emittance measurement unit
NPM: Non-invasive profile monitor
TMP: Turbomolecular pump

## Slide 3: Table of content
System Requirements
Operating procedures
Skid state of Operation
Operating procedures
Test & Verification
Open issues

## Slide 4: CWS01 Cooling Water Skid

## Slide 5: System Requirements
Provide cooling to ISrc and LEBT
The system has been designed to reject 85kW when supplying circulating coolant deionized water at a maximum of 40°C in a maximum ambient temperature of 20°C and at a flow rate of 300 lpm at a design pressure of 10 barg.
Main components are Run/Standby centrifugal pumps, stainless steel plate heat exchanger, deionisation sub circuit, degassing system, isolation valves, water filters, expansion vessel, fill loop

## Slide 6: System Requirements
Design pressure/flow:
  Process circuit: 6 barg/305 lpm
  Primary CWL circuit: DP 1,1 bar/305 lpm
Maintain cooling water quality (<0.3 uS/cm, DO 40-50 ppb)
Local control and HMI on the skid.
All PV-transfer by Profinet to Control System (EPICS)

## Slide 7: Operation procedures
Skid will start on rising edge pulse from Control System
The system will run automatically, to control pressure, flow, temperature, conductivity, oxygen content all within stated parameters.
Ion-exchangers and filters to be monitored and maintained (yearly)
Sensors to be checked (yearly)
Nitrogen gas supply (bottles) to be monitored and exchanged. (weekly)
Deoxygenation system must be purged when longer periods without operation.

## Slide 8: Skid state of Operation
Hard wired control and alarm from/to Control System
  Start / Stop Enable Run Mode
System Running The system is in Run Mode
Enable Load The System is in Run Mode AND
Flow has been established AND
Flow AND Temperature is within acceptable limits AND Conductivity is within acceptable limits
Alarm Present There is an active or unacknowledged alarm on the system
Trip Present There is an active trip.
High Temp Alarm Trip

## Slide 9: Test & Verification
All internal signals, alarms and trips has been verified during FAT and SAT acc to test procedure.
CW manifolds and connections integrity tested with nitrogen (7bar)

## Slide 10: Outstanding issues
# | System/Comp. | Status | Description | Due date | Remark
1 | CWS01 | Pending | Documentation | July 2018 | 
2 | CW Pipes to ISrc | Not connected | Connections to be modified | July 2018 | 
3 | CWL Pipes | Ongoing | Insulation of pipes | July 2018 | 

## Slide 11
Thank You!
Questions?

## Slide 12: P&ID

## Slide 13: P&ID

## Slide 14: P&ID

## Slide 15: P&ID

## Slide 16: P&ID

## Slide 17: P&ID

## Slide 18: P&ID