Motion control and EPICS
Torsten Bögershausen
Motion Control and Automation Group
www.europeanspallationsource.se

---
Motion Control Integration, basic
3 layers in control box:
EPICS IOC
Axis record (single axis)
Model 3 driver
Basic functionalities for point-to-point movements
Extensions of functionality in additional records
CSS BOY
caget / caput
Python based
application
EPICS Control Network
ChannelAccess
pvAccess
IOC: EPICS (base)
axisRecord
m1
Model 3 driver
Ethernet + TCP/IP (closed source)
In memory (ecmc)
Motion Control Unit
Encoder
Motor
(End) switches

---
What’s the Motor module for?
What’s the Motor module for?
Device independence – motor hardware is transparent to users.
  - Same user displays and motor motion behavior, for all devices.
Available operations from this display;
Make absolute or incremental moves.
Define the current position.
Stop the current move.
without any controller specific information.

---
CSS screen, basic
Device independence – motor hardware is transparent to users.
Same user display and motor behavior for all devices.
- Status at a glance:
Where should the motor be
Where is the motor
Motor is done, moving, homed...
Limit switches
Status & problems
- Commands:
- Make absolute moves.
- Tweak the motor
- Stop the current move.

---
Status in 2 bits
3 States in control screen:
IDLE Moving Problem
if (!DMOV || MOVN)
 status = Moving
else if (STAT != 0 || MISS)
 status = ERROR
else
 IDLE

---
Move types
- Absolute (VAL, DVAL, RVAL)
- Relative (RLV)
- Incremental (TWF, TWR, TWV)
- Constant velocity (“Jogging”) (JOGF, JOGR, JVEL, JAR)

---
axis record: configuration
- Basic configuration
- MRES == step size
  RDBD == Retry Dead Band
  HLM, LLM == Soft limits
  VELO == velocity
- Ideal for “simple” motion controllers
- Advanced motion controllers have many more parameters (training session)

---
axis record runtime
- Single axis:
  - point to point moves
  - move with constant velocity
  - homing
- Status & error reporting
- Encoder “readback”
- Note : readback (-RB != -Act)

---
Features - coordinate systems.
Features - coordinate systems.
steps or ticks
Raw
EGU’s
Dial
User
X
RVAL
MRES
DIR: +/- 1
OFF
X
DVAL
VAL
+

---
Feedback data flow
setDoubleParam(
pC_>motorPosition_)
Int32(floor)notorPosition
RMP
MRES
X
priv->readBack.position
UEIP = No && URIP = No
DRBV
UEIP = No && URIP = Yes
UEIP = No && URIP = Yes
ERES
UEIP = Yes
setDoubleParam(
pC_>motorEncoderPosition_)
X
RDBL Link
X
RRES
priv>
readBack.encoderPosition
Int32(floor)encoderPosition
REP

---
Feedback data flow, RBV and RRBV
RMP
UEIP = No
URIP = No
DIR: +/- 1
+
UEIP = Yes
X
DRBV
RRBV
RBV
REP
UEIP = No
URIP = Yes
OFF
÷
MRES
RDBL Link
X
RRES

---
axisRecord @ ESS
- Fork of the motor record
- Abstracts the motor into an EPICS PV
  LabS-ESSIIP:MC-Pos-01
  LabS-MCAG:MC-Pos-TS01
- Converts writing to a field into commands
  to the controller
- Retrieves the status from the controller
- EPICS PV can be reached via:
- C/C++/Java/Python/sh

---
axisRecord @ ESS
- Fork of the motor record
- Lost things:
  - Soft motor
  - fixes/improvements from community
  - Sync with EPICS: @collaboration meeting
    in June @Argonne
- In future: Go back to motor code base,
  - work ongoing
  - not fully ready for this training

---
Fields used in Record
- VAL: Where the motor should be
- RBV: Where the motor is
- MOVN: Moving
- DMOV: Done moving
- LVIO: (soft) limit violation
- STAT: Alarm status
- MISS: ”Missed” (see RDBD, ”retry deadband”)

---
Automated tests
- Find many bugs
- Python based
- With real hardware
- Part of axisRecord.

---
Motion Control Integration (today)
Motion Control Integration, basic
3 layers in control box:
EPICS IOC
Axis record (single axis)
Model 3 driver
Basic functionalities for point-to-point movements
Future extensions of functionality in additional records
CSS BOY
caget / caput
Instrument Control (e.g. Python based)
EPICS Control Network
Channel Access
IOC: EPICS (base)
axisRecord
m1
Model 3 driver
Ethernet + TCP/IP
Motion Control Unit
Encoder
Motor
(End) switches

---
Motion Control Integration (tomorrow)
Motion Control Integration (today)
3 layers in IOC:
Axis record (single axis)
longout record (homing)
Model 3 driver
Basic functionalities for point-to-point movements
Future extensions of functionality in additional records
Current development includes a.o. jerk, homing procedures
Extensions need to be implemented in user interfaces, model 3 driver and motion control unit as well (strong coordination necessary)
CSS BOY
caget / caput
Instrument Control (e.g. Python based)
EPICS Control Network
Channel Access
IOC: EPICS (base)
 MotorRecord
m1
 longout
m1-PrcHom
Model 3 driver
Ethernet + TCP/IP
Motion Control Unit
Encoder
Motor
(End) switches

---
python
- motor = 'LabS-ESSIIP:MC-Pos-01'
- epics.caput(motor, destination, wait=True)
- stat = epics.caget(motor + '.STAT', use_monitor=False)

---
Move & monitor a motor
Move & monitor a motor
(done on a simulator, Mac or raspi)
- camonitor IOC:m1.RBV IOC:m1.DMOV
- IOC:m1.RBV 2016-02-02 10:58:16.157350 24.87
- IOC:m1.DMOV 2016-02-02 10:58:16.658745 1
- IOC:m1.DMOV 2016-02-02 10:58:16.658745 0
- IOC:m1.RBV 2016-02-02 10:58:30.124368 49.86
- IOC:m1.RBV 2016-02-02 10:58:31.138087 60.06
- IOC:m1.DMOV 2016-02-02 10:58:31.639072 1
- caput IOC:m1.VAL 60.1
- Old : IOC:m1.VAL 24.9
- New : IOC:m1.VAL 60.1
#Notes:
#caput: Channel access put
#camonitor: Channel access monitor
#IOC:m1..DMOV: Field “done moving”
#IOC:m1.RBV: Field Read back value

---
That's it
Thanks for listening