## Slide 1: Sample cave study
IKON’16 13/0219
Sylvain Désert

## Slide 2
NID June 2018: offer made by LLB to study Instrument Sample Caves
7 instruments answered: C-SPEC, BIFROST, MAGIC, T-REX, DREAM, SKADI, ESTIA
Study performed by Artélia from JUL to OCT 2018
introduction

## Slide 3
Input data
Instrument cave designs
General Civil Design Criteria
Installation Logistic
Access logistics
Crane coverage
Shielding concepts
Load specification
Gallery penetrations and conduits
Instrument teams
Confluence
| PAGE 3

## Slide 4
Regulatory context
Construction code
  Eurocode 1: Actions on structures (EN 1991)
  Eurocode 2: Design of concrete structures (EN 1992)
  Eurocode 3: Design of steel structures (EN 1993)
Seismic requirements
  ESS-0122941: Load Specification Miscellaneous Seismic Topics D Buildings
  ESS-0061819: General Civil Design Criteria (GCDC) for D01 D02 and D03

## Slide 5
Technical constraints
7.5 T and 30 T crane available in hall D01
10 T crane available in E01
Handling equipments available for construction in D01 and E01
 operated by ESS
No seismic requirement for the caves in hall (D01 and E01)
 shielding must not fall on the structural pillars of the building
Structural dimensions of caves will not change during their operation time
Generation of dust, noise and slight vibrations during the dismantling
operations has no impact on the overall operation in the facility
Impact on cave on the galleries not studied

## Slide 6
hypothesis
Planning
  Experimental cave area clean and free
  No interface to manage with other systems
  Handling equipments available
  Construction & installation full responsability of the supplier (not ESS)
Quotation
Only for the concrete part of the caves
For turnkey contract:
   detailed design, drawings, manufacturing, transportation
Based on numerous feedbacks and current market price in France + Tyrens

## Slide 7
Anchored walls (~ 200 mm) in the slab
 structural continuity
Construction methodologies
Assembled concrete blocks laid on the slab
 advanced structural calculation to check wall performance
regarding the mass of the roof and shock constraints

## Slide 8
Building methodologies
5 methodologies:
  Full Cast Concrete
  Precast Walls
  Customized Blocks
  Empty Shuttery Blocks + Concrete
  Mixed Cast concrete + Beam slabs
3 types of structures:
  Additional slabs: meth. 1
  Walls: meth. 1  4
  Roof: meth. 1  3 + 5

## Slide 9
Building methodologies
Precast Walls
Thickness 600+mm uncommon
   specific development
Homogeneity of poured concrete not guaranted
Transportation and access to halls
 smaller sizes  more joints
Specific cranes required (1.5 k€/day)
Difficulties to check the materials origin
Difficulties to install if the floor flatness not perfect

## Slide 10
Full beam slabs for roof
Incompatible with easy opening roof
 requires dismounting
Specific cranes required (1.5 k€/day)
Specific development (size and shape)
 expensive
Building methodologies

## Slide 11
Methodologies studied

## Slide 12
Solution 1:
full cast concrete
Concrete pouring of slabs, walls and roof on site at the final cave location
    Suitable for all cave configuration
    Limited number of joints
    Better radiation shielding
    Ideal for high thicknesses
    Better concrete hardness
    Good tracability: origin & quality of materials
    Good adaptation to slab flatness
    Noise and dust during work
    Difficult to deconstruct
    Anchors in the slab required
    Vibration, noise and dust during demolition

## Slide 13
Solution 2:
mixed Full cast concrete / slabs
Concrete pouring of slabs, walls and opening parts of roof
Beam slabs used for other parts of roof
    - same as SOLUTION 1 -
    Possibility to have easy removable roof parts
    - same as SOLUTION 1 -
    Not adapted for high thickness roof (weight)

## Slide 14
Solution 3:
blocks + Full Cast Concrete roof
Custom concrete blocks pre-fabricated walls + full cast concrete roof
    Suitable for all cave configuration
    Limited noise and dust production
    Easy disassembly of the walls
    No anchor in the slab
    Ideal for roof with high thickness
    Good tracability: origin & quality of materials
    Altimetry differences removed by casting of the roof
    Important design phase (maximize block size, minimize molds)
    Difficult to deconstruct the roof
    Adaptation required for slab flatness
    Heavy handling system to install the blocks
    The crane inside the cave cannot be fixed to the wall

## Slide 15
Solution 4:
bloCks + mixed cast concrete / slabs
Custom concrete blocks pre-fabricated walls + cast concrete and beam slabs roof
    - same as SOLUTION 3 -
    Possibility to have easy removable roof parts
    - same as SOLUTION 3 –
    Not adapted for high thickness roof (weight)

## Slide 16
Solution 5:
shuttering blocks + full cast concrete
Shuttering blocks walls + full cast concrete roof
    Suitable for all cave configuration
    Limited noise and dust production
    Limited requirement of handling tools (walls)
    No structural integrity
    Not compatible with large wall thickness (concrete inhomogeneity)
    Anchor in the slab
    Difficult to deconstruct the roof
    Demolition cost
    Vibration, noise and dust during demolition
    The crane inside the cave cannot be fixed to the wall

## Slide 17
Solution 6:
shuttering blocks + mixed cast concrete / slabs
Shuttering blocks for walls + cast concrete and beam slabs roof
    - same as SOLUTION 5 -
    Possibility to have easy removable roof parts
    - same as SOLUTION 5 –
    Not compatible with high thickness roof (weight)

## Slide 18
Technical analysis
Selection criterias for QUALITY:
  Structural capacity
  Radiation protection
  Ease of assembly
  Impact on the slab
  Compatibility with in-house handling equipment
  Ease of demolition
  Noise, dust and vibration during demolition

## Slide 19
Quality Summary
Shuttering blocks methodology discarded
COST & DELAY studied for Solutions 1 to 4

## Slide 20
delay Summary
Dream cave

## Slide 21
cost hypothesis
Hypothesis:
  Concrete density 2500 kg / m3
  Cost of steel 2500 € / T
  Concrete cost 120 € / m3
  Steel density (slabs) 150 kg / m3
  Steel density (flor/walls) 75 kg / m3
  Mobile crane + other 1500 € / day
Note: ESS provides workforce for assembly/installation in case of blocks
ESS invoicing costs unknown (handling equipment operation, instalation, services…)
  Solution 1: no ESS cost
  Solution 2: 2 ESS workers for 5 days
  Solution 3: 2 ESS workers for 15 days
  Solution 4: 2 ESS workers for 24 days

## Slide 22
Cost Summary
Dream cave

## Slide 23
quality / cost / delay
Dream cave
 Final results are close
 Full cast concrete better for all the 7 caves
 Weights for Quality / Cost / Delay can be customized depending on priority
   may change the most appropriate solution

## Slide 24
B4C Shielding
Hypothesis:
  5 mm of Boreflex on all inner surface but the floor:
  Price: 655 €/m2
  Installation time: 2.5 m2/h with 2 people
Transporattion to ESS 1.5 k€
( Jefferson Lab solution looks a possible better alternative)

## Slide 25
Cave impact on floor
E01: 20 T / m2
D01: 14 T / m2
All caves are made of regular concrete with average density of 2500 kg / m3
Internal crane and additional components on the walls or roof not considered
 No impact on the floor for most caves but DREAM
 Basement of the walls can be increased for larger footprint

## Slide 26
aknowledgements
Yassine HAKIM
Sébastien Le Couster
Nathanaël Schmidt
Thomas Robillard
Sébastien Gautrot
Sylvain Rodrigues
Patrice Permingeat