## Slide 1: Cryogenics for the ESS Superconducting Linac
Jaroslaw Fydrych and Xilong Wang
European Spallation Source ERIC
ECD, Lund, Sweden, 07th Oct, 2019

## Slide 2: Outline
Introduction to the Linac cryogenic system
Cryogenic Distribution System
    2.1. Specification and design
    2.2. Collaboration with in-kind partners
    2.3. Current status and next actions
Accelerator Cryogenic Plant
    3.1. Specification
    3.2. Current status
    3.3. Selected issues

## Slide 3: ESS Cryogenic System Block Diagram
Pure Helium
Gas Storage
Standalone Helium Purifier
Helium Recovery System
Accelerator
Cryoplant
5 m3
LHe Tank
Target Moderator
Cryoplant
LHe Mobile Dewars
Test Stand Cryodistribution System
Instruments & Experiments
LN2 Storage Tanks
LN2 Mobile Dewars
Cryodistribution System for Elliptical Linac
Elliptical
Cryomodules
Lund Test Stand 2
Target Cryodistribution System
Hydrogen Circulation Box
Hydrogen Moderator
Cryodistribution System for
Spoke Linac
Spoke
Cryomodules
20 m3 LHe Tank
Test & Instrument Cryoplant
Cryogenic System for Linac

## Slide 4: Layout of the ESS Linac Cryogenic System
Cryogenic Distribution Line (310 m)
comprising 43 valve boxes
Endbox
Cryogenic
Transfer
Line (65 m)
21 High-Beta Cryomodules (174 m)
9 Medium-Beta
Cryomodules
(75 m)
13 Spoke
Cryomodules
(54 m)
ACCP
Auxiliary process lines
Splitting
box
Cryogenic Distribution System for the ESS linac is intended for delivering the cooling power from the Accelerator Cryogenic Plant (ACCP) to the cryomodules by means of the constant flows of supercritical helium at 4.5 K and 3 bar(a) and cold gaseous helium at 40 K and 19.5 bar(a).

## Slide 5: Layout of the ESS Linac Cryogenic System
Endbox
Cryogenic
Transfer
Line (65 m)
Splitting
box
ACCP
Auxiliary process lines
CDS-EL
CDS-SPK
CDS-EL CDL (250 m)
comprising 30 valve boxes
CDS-SPK CDL (60 m)
comprising 13 valve boxes
30 Elliptical Cryomodules
13 Spoke
Cryomodules
Interface
with ACCP
Interfaces with 9 MB CMs
Interfaces with
21 HB CMs
Interface to 13 SPK CMs
Interface with CDS Vent Line
Interfaces
with Linac tunnel flour and ceiling
Interface
with vacuum pumps
Interface between CDS-EL and CDS-SL
Interfaces
with control system

## Slide 6: Linac CDS - General flow scheme
Two main cryogenic circuits:
- thermal shield circuit (TS supply and TS return lines)
- cold helium circuit (Helium supply and VLP lines)
Elliptical cryomodules
Spoke cryomodules

## Slide 7: Valve Box flow scheme diagram
The heat exchanger, JT and filling valves are in the cryomodule!
Valve box for the elliptical cryomodule

## Slide 8: Valve Box flow scheme diagram
The heat exchanger, JT and filling valves are in the valve box!
Valve box for the spoke cryomodule

## Slide 9: Partners
ESS Cryodistribution is being provided as two separated in-kind contributions.
WUST from Poland provides the design, procurement, manufacturing, transport and installation of the CDS for Elliptical Linac (and the CDS for Lund Test Stand 2).
CNRS/IPNO from France provides the design, manufacturing, transport and installation of the CDS for Spoke Linac.

## Slide 10: Technical documentation developed at ESS - Lists of requirements
Main general requirements
adequate to ensure smooth operation throughout the expected lifetime of 45 years,
suitable for continuous operation (with limited scheduled interruptions only) to meet top-level requirement of 95 % availability of the linac itself,
ensure no deterioration of thermal and mechanical properties within the operation lifetime,
must allow for the separation of a single cryomodule from the cryodistribution line,
must allow for the warm-ups and cool-downs of a single cryomodule, while keeping the rest of the system at cryogenic temperatures,
must comply with Swedish and European legislation concerning occupational health, safety and environmental protection,
Main technical requirements
heat loads not higher than 420 W and 3.66 kW to the cold helium circuit and thermal shield, respectively,
supercritical helium temperature below 5.2 K in the interfaces to the cryomodules at nominal operation conditions,
vacuum insulation below 10-6 mbar at nominal working condition (below 5·10-3 mbar at ambient temperature with active vacuum pumping),
integral helium leak rate below 110-7 mbarl/sec from the helium circuit to the vacuum,
tightness of the valve seats ≤ 110-4 mbarl/sec,
200 full thermal cycles,
all materials and components must tolerate the radiation dose of 5105 Gy,
Total number of
technical requirements: 228!

## Slide 11: Technical documentation developed at ESS - Specifications
ESS-0011735: Technical Specification of the Cryogenic Distribution System for the Elliptical Linac
ESS-0028495: Interface between the ACCP and the CDS
ESS-0011309: Interface between the CDS and the elliptical cavity cryomodules
ESS-0011308: Interface between the CDS for the elliptical linac and for the CDS for the spoke linac
ESS-0012571: Location of the wave guides under the Cryogenic Distribution Line for the elliptical linac
Appendix A. Perspective view of the CDS for the elliptical linac
Appendix B. Routing and overall dimensions of the CDS for the elliptical linac

## Slide 12: Technical documentation developed at ESS - Conceptual design

## Slide 13: 3D model of the Elliptical Linac section
transportation pathway

## Slide 14: 3D model of the CDS-EL
CDS-EL detailed design developed by WUST, in the scope of Polish in-kind contribution to the ESS Accelerator Project.

## Slide 15: 3D model of the Spoke Linac section
transportation pathway

## Slide 16: 3D model of the CDS-SPK
CDS-SPK detailed design developed by IPNO, in the scope of French in-kind contribution to the ESS Accelerator Project.

## Slide 17: Current status of the CDS project
CDS-EL CTL
11 CTL sections manufactured (92%)
5 CTL sections ready to be installed in Week 42
CDS-EL VBoxes
28 Vboxes manufactured (93%)
27 VBoxes installed and positioned (90%)
24 interconnections welded (80%)
17 auxiliary line sections installed (57%)
CDS-SPK
VBoxes under manufacturing
End Box under manufacturing
Auxiliary Lines manufacturing contracted
CDS-SPK installation activities contracted
Installation of the CDS-EL VBoxes carried out by the WUST’s contractor, KRIOSYSTEM, Poland

## Slide 18: Current status of the CDS project
Positioning of the CDS-EL VBoxes carried out by the ESS Survey and Alignment team
CDS-EL CTL
11 CTL sections manufactured (92%)
5 CTL sections ready to be installed in Week 42
CDS-EL VBoxes
28 Vboxes manufactured (93%)
27 VBoxes installed and positioned (90%)
24 interconnections welded (80%)
17 auxiliary line sections installed (57%)
CDS-SPK
VBoxes under manufacturing
End Box under manufacturing
Auxiliary Lines manufacturing contracted
CDS-SPK installation activities contracted

## Slide 19: Current status of the CDS project
MBL section of the CDS-EL – in the detailed 3D model…
27 of the 30 CDS-EL Valve Boxes installed and positioned in the tunnel, in accordance to the ESS Linac Installation Plan!
… and in real life!

## Slide 20: Towards completion of the CDS project
Finish of the CDS-EL installation in Dec 2019
CDS-SPK installation from Dec 2019 to Feb 2020
Commissioning of both CDS-EL and CDS-SPK in March 2020
CDS-EL
CDS-SPK

## Slide 21: ESS Cryogenic System Block Diagram
  ACCP
Pure Helium
Gas Storage
Standalone Helium Purifier
Helium Recovery System
Accelerator
Cryoplant
5 m3
LHe Tank
Target Moderator
Cryoplant
LHe Mobile Dewars
Test Stand Cryodistribution System
Instruments & Experiments
LN2 Storage Tanks
LN2 Mobile Dewars
Cryodistribution System for Elliptical Linac
Elliptical
Cryomodules
Lund Test Stand 2
Target Cryodistribution System
Hydrogen Circulation Box
Hydrogen Moderator
Cryodistribution System for
Spoke Linac
Spoke
Cryomodules
20 m3 LHe Tank
Test & Instrument Cryoplant

## Slide 22: ACCP - Specification
Heat loads:
  3 kW @ 2 K, 9 g/s @ 4.5 K and 11380 W @ 40 -50 K
Continuous operation:
  24 h per day / 7 days per week
  2 years without scheduled shut-down
Availability: > 99 % not count utilities & process control
Two stages and four main operation modes each stage
  ND, NTD, TS SB, 4.5 K SB, Max. Liquefaction mode

## Slide 23: ACCP – System Features
Three warm compressors, six turbines, three cold compressors and several bunches of plate fin heat exchangers
Mixed compression cycle at 2 K plus helium guard system for SP compressor
Capacity control
  Floating pressure cycle for HP compressor
  VFD for SP, LP compressors and CCs
  Exchange of CCs flow parts
All built-in acceptance test equipment
Energy recovery

## Slide 24: ACCP – System Parameters
Main electrical power | 2.37 MW |  |  |  |  | 
Power at 4.5 K equivalent | ~9 kW with exergy efficiency 25.9% |  |  |  |  | 
 | Vi | Psuc, bara | Pdis, bara | , g/s | Ps, kW | VFD
SP compressor (33K/71K) | 4.0 | 0.607 | 4.25 | 117 | 303 | Yes
LP compressor (33K/83K) | 2.6 | 1.05 | 4.25 | 285 | 516 | Yes
HP compressor (40K/83K) | 2.6 | 4.05 | 20.5 | 735 | 1383 | NO
 | Vi | Psuc, bara | Pdis, bara |  | Ps, kW | VFD
SP compressor (33K/71K) | 4.0 | 0.607 | 4.25 | 117 | 303 | Yes
LP compressor (33K/83K) | 2.6 | 1.05 | 4.25 | 285 | 516 | Yes
HP compressor (40K/83K) | 2.6 | 4.05 | 20.5 | 735 | 1383 | NO
Impurity removal (ORS/dryer/cryogenic adsorbers) | Oil | BOR (1000 ppm) - Coalscer in skid (10 ppm) - FOR (0.5 ppm Aerosols and 10 ppb Vapour) |  |  |  | 
 | Water | One bed on line dryer (0.1 ppmv) |  |  |  | 
 | Air | Two 80 K Adsorbers (73 K, 20 bar) and one 20 K adsorber (24 K, 20 bar) |  |  |  | 
Liquid He storage | 20’000 Dewar (2.2 tons) + Subcooler in cold box (1500 liter) |  |  |  |  | 
Warm He storage tank | 14 X 70 m3 at 20 bar (2.7 tons) (CMs + CDS + ACCP in total) |  |  |  |  | 

## Slide 25: ACCP - WCS

## Slide 26: ACCP – Cold Box

## Slide 27: Current Status
Successful 100 hours acceptance tests of ACCP-WCS (Partially)
Plant automatic CD/WU
Some operation modes preliminary tested
Max. Liquefaction rate – to be improved
Cold compressors started up

## Slide 28: Selected Issues
Two oil coolers corrosions and replacement

## Slide 29: Selected Issues
HP compressor damage and spare compressor slide valve control
  Damaged
  New
  Old: 95 %
  Spare: 99.8 %
Slide valve position
HP flow
Power

## Slide 30: Selected Issues
Under estimation of ESS CF work and ESS site work coordination
  Concrete foundation of compressor skids
  Site work coordination and conflicting

## Slide 31: Selected Issues
Leak searching and repair
Leak here!

## Slide 32: Acknowledgements
Thank you
Prof. Hans Quack
Guy Gistau Baguer
DESY
CERN
FERMILAB
Uppsala university
KSTAR-NFRI
Excellent Team works by LKT/ESS