## Slide 1
2019 European Cryogenics Days
08.10.2019 in Lund, Sweden
The cryogenic needs of the FCC
Claudio Kotnig on behalf of the CERN Cryogenics Group

## Slide 2: Gentle Reminder: Particle Colliders
  Particle beams are accelerated to close to the speed of light
  Two opposing particle beams are brought to collision
  E = m · c2
  ... in linear colliders only one attempt
  ... in circular colliders non-collided particles are collected, returned and used for several attempts
  → Particle trajectories deflected by superconducting magnets (cryogenic temperatures necessary)

## Slide 3: LEP & LHC
  Geneva Basin
5
6
7
8
1
2
3
4
  LHC Cryo
1.8
  LEP Operation
  1990 - 1995 (z0 - Bosons)
  1996 - 2000 (w± - Bosons)
  LHC Operation
  2009 - 2023
  2026 - 2038 (HiLumi)
5
6
7
8
1
2
3
4
  LEP Cryo
  Cryoplant
  RF Cavities
  Experiment
  Cryogenic Distribution Line
  4 x 12 kW @ 4.5 K cryoplants
  10 x 18 kW @ 4.5 K cryoplants
  8 x 3.3 km of Cryogenic Distribution line

## Slide 4: European Strategy for Particle Physics
  FCC Conceptual Design Report
  (issued 15.01.2019)
  https://fcc-cdr.web.cern.ch/
What next?
  In 2013 the European Strategy for Particle Physics decided to launch studies to investigate different machines and concepts for future research in particle physics
  Circular Collider Study:
  Future Circular Collider
  Integration into existing Accelerator Complex at CERN
  LHC
  FCC
  SPS
  PS
  LEIR

## Slide 5: Some FCC superlatives in vivid comparisons
  LHC
  FCC
  Cheops
  LHC
  FCC
  2014 Start FCC conceptual design phase
  2019 CDR released 15.01.2019
  2020 - 2028 Preparation
  2029 - 2037 Tunneling & installation FCC-ee
  2038 - 2053 FCC-ee operation in 4 stages
  2054 - 2063 FCC-hh preparation & installation
  2064 - 2090 FCC-hh operation
Timeline
 | LEP/(HL-)LHC | FCC
Circumference | 27 km | 100 km
Excavated soil volume tunnel |  | 
Electrical power consumption |  | 
Max. stored beam energy |  | 
Some data
  Saab 200
  A350
  Cheops
  0.42 · 106 m3
3.25 · 106 m3
  200 MW
580 MW
  0.33 GJ
8.4 GJ
  LA
  GE
  ZU
  GE

## Slide 6: FCC tunnel
A
B
C
D
E
F
G
H
I
J
K
L
  Courtesy of J.Osborne
  ≈ 600 m

## Slide 7: FCC machines
FCC-ee machine
FCC-hh machine
  Precise measurements: Beam energy tuned to create certain particles
  Discovery machine: Beam energy maximized to create new particles

## Slide 8: Benefits for particle physics research
  Courtesy of L.Tavian
  Same Energy
  Luminosity increase by 102 ÷ 105
  Energy increase by factor 7
  Luminosity increase by factor 1 ÷ 2

## Slide 9: FCC-ee Cryogenics: Research Goal in 4 Stages
Research goal
In-depth exploration to find
Optimized to study 4 particles at highest luminosity
The 4 Stages Plan
1. Stage (2038 - 2041): z0-Bosons (EBeam = 45.6 GeV)
2. Stage (2042 - 2044): w±-Bosons (EBeam = 80 GeV)
3. Stage (2045 - 2047): Higgs Bosons (EBeam = 120 GeV)
2048 – 2049: 1 year installation, upgrade & rearrangement
4. Stage (2049 - 2053): Top Quarks (EBeam = 175 | 182.5 GeV)
confirmation of or
deviations from the Standard Model
Increasing
cryogenic
requirements

## Slide 10: FCC-ee Cryogenics: Applications
Cryogenic Applications
RF Cavities
Accelerating the lepton bunches
  Courtesy of JLAB
Compensate for the energy losses due synchrotron radiation PSR
Stage 1 (z0) | 0.036 GeV
Stage 2 (w±) | 0.34 GeV
Stage 3 (Higgs) | 1.72 GeV
Stage 4 (Top Quark) | 7.8 / 9.2 GeV
  Energy losses per turn:

## Slide 11: FCC-ee Cryogenics: Stage 1/4 (z-Boson)
Beam 2
Beam 1
3. Stage: Higgs Bosons (EBeam = 125 GeV)
2. Stage: w±-Bosons (EBeam = 80 GeV)
1. Stage: z0-Bosons (EBeam = 45.6 GeV)
4. Stage: Top Quarks (EBeam ≥ 173 GeV)
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)
Booster
QRL
A
B
C
D
E
F
G
H
I
J
K
L

## Slide 12: FCC-ee Cryogenics: Stage 2/4 (w-Boson)
Beam 2
Beam 1
3. Stage: Higgs Bosons (EBeam = 125 GeV)
2. Stage: w±-Bosons (EBeam = 80 GeV)
1. Stage: z0-Bosons (EBeam = 45.6 GeV)
4. Stage: Top Quarks (EBeam ≥ 173 GeV)
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)
Booster
QRL
A
B
C
D
E
F
G
H
I
J
K
L

## Slide 13: FCC-ee Cryogenics: Stage 3/4 (Higgs Boson)
Beam 2
Beam 1
1. Stage: z0-Bosons (EBeam = 45.6 GeV)
2. Stage: w±-Bosons (EBeam = 80 GeV)
3. Stage: Higgs Bosons (EBeam = 125 GeV)
4. Stage: Top Quarks (EBeam ≥ 173 GeV)
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)
Booster
QRL
A
B
C
D
E
F
G
H
I
J
K
L

## Slide 14: FCC-ee Cryogenics: Stage 4/4 (Top Quark)
4. Stage: Top Quarks (EBeam ≥ 173 GeV)
3. Stage: Higgs Bosons (EBeam = 125 GeV)
1. Stage: z0-Bosons (EBeam = 45.6 GeV)
2. Stage: w±-Bosons (EBeam = 80 GeV)
A
B
C
D
E
F
J
K
L
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)
Beam 1&2
Booster
QRL
Header A: 800 MHz RF Cavities Supply (2.2 K / 1.3 bar)
Header B: 800 MHz RF Cavities Supply (2.0 K / 30 mbar)
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)

## Slide 15: FCC-ee Cryogenics: Cryo Staging Overview
 | Stage 1 (z0) |  | Stage 2 (w±) |  | Stage 3 (Higgs) |  | Stage 4 (Top Quark) | 
Time | 2038 - 2041 |  | 2042 - 2044 |  | 2045 - 2047 |  | 2049 - 2053 | 
Frequency | 400 MHz | 800 MHz | 400 MHz | 800 MHz | 400 MHz | 800 MHz | 400 MHz | 800 MHz
Tsat (pSat) | 4.5 K (1.3 bar) | 2.0 K (30 mbar) | 4.5 K (1.3 bar) | 2.0 K (30 mbar) | 4.5 K (1.3 bar) | 2.0 K (30 mbar) | 4.5 K (1.3 bar) | 2.0 K (30 mbar)
Number Cryoplants | 1 CP @ Point J | - | 1 CP @ Point J | - | 1 CP @ Points D & J | - | 2 CPs @ Points D & J | 2 CPs @ Points D & J
RF voltage | 0.1 GV | - | 0.75 GV | - | 2 GV | - | 4 GV | 5.4 / 6.9 GV
Cryopower | 1 x 4 kW @ 4.5 K |  | 1 x 41 kW @ 4.5 K |  | 2 x 41 kW @ 4.5 K |  | 4 x 41 kW @ 4.5 K 4 x 12 kW @ 2.0 K | 
Cryopower @ 4.5 K | 4 kW @ 4.5 K |  | 41 kW @ 4.5 K |  | 82 kW @ 4.5 K |  | 252 kW @ 4.5 K | 
Electrical Power Consumption | 0.9 MW |  | 9.5 MW |  | 19 MW |  | 58 MW | 
Helium Inventory |  |  |  |  |  |  |  | 
Cryomodule | 1.2 t |  | 1.6 t |  | 4.1 t |  | 11.0 t ÷ 12.6 t | 
Distribution | 7.9 t |  | 7.9 t |  | 7.9 t |  | 8.9 t | 
Cryoplant | 1.0 t |  | 1.0 t |  | 2.0 t |  | 4.0 t | 
Total | 10 t |  | 10 t |  | 14 t |  | 24 t ÷ 26 t | 
FCC-ee Cryo Summary

## Slide 16: FCC-hh Cryogenics: Research Goal
Research goal
Production of new particles
Precise measurement of the Higgs self-coupling
Exploration of the electroweak symmetry breaking
WIMPs (warm interacting massive particles) as candidates for dark matter can be discovered or ruled out
4 collision modes
Hadron – Hadron
Hadron – Lepton
Ion – Ion
Ion – Proton

## Slide 17: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Main purpose of the FCC is particle physics Cryogenics has to be adapted to enable it

## Slide 18: Challenge #1: Physics is the boss
  DT ≈ 300 K
  DT < 0.3 K
Why superconductivity?
m = 0.51 MeV/c2
e-
m = 938.27 MeV/c2
p+
  16 T
  1.5·105 A/cm²
  2 K
  TCoil < 2.15 K
  PSR ≈ 30 W/m
  pmin = 16 mbar
  → Tsat ≈ 1.8 K
  Heat sink: Saturated two-phase helium flow
  (Must be intercepted)
  → Pmin = 750 MW

## Slide 19: Challenge #1: Physics is the boss
  Courtesy of Cedric Garion
  Temperature range (40 ÷ 60 K) chosen to
  Preserve vacuum quality
  Keep image current impedance low
  Decrease exergetic costs
  TBS = 40 ÷ 60 K
  pBS = 50 bar
  High pressure level (50 bar) chosen to
  Decrease pressure losses
  Decrease compression ratio
  Thermal shields: Operated in series after cooling the beam screens
  300 K
  2 K
  60 K
  Cooling Channel

## Slide 20: Challenge #1: Physics is the boss
  Itot ≈ 20 MA
  Nb3Sn Cables @ 2 K
  Transmission Line @ 300 K
  Courtesy of CERN
  DT ≈ 300 K
  Dl ≈ 1.5 m
  Current Leads
  Electrical power to feed electromagnets is delivered by transmission lines at ambient temperature level
  The conductors transmitting the current to the Nb3Sn cables have to cooled down from 300 K to 2 K
  Wiedemann-Franz law: Good electrical conductors are good thermal conductors → sophisticated design needed to reduce heat leaks
  Courtesy of Amalia Ballarino

## Slide 21: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Challenge # 2: Much power for low temperature
  A second Geneva– electrically spoken

## Slide 22: Challenge #2: Get the power
Pmax = 220 MW
140 kW @ 1.8 K
5800 kW @ 40 ÷ 60 K
1170 kW @ 4.5 ÷ 300 K
  Cold Mass Cooling & Header B heat leaks
  Beam Screen Cooling & Thermal Shields
  Current Lead Cooling
Cycle | QLoad in kW | Pmin in MW | Preal in MW
CMC+B | 140 | 18 | 130
BS+TS | 5800 | 29 | 81
CL | 1170 | 2 | 7
  Electrical Power Consumption of CERN during FCC-hh operation
  220 MW (38 %)
  580 MW
A
B
C
D
E
F
G
H
I
J
K
L
Pmax = 220 MW
Pmax = 220 MW

## Slide 23: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Challenge # 2: Much power for low temperature
  Challenge # 3: Efficiency vs. Simplicity
  CAPEX vs. OPEX
  Economics vs. Availability
  Ingenuity vs. Beauty

## Slide 24
Challenge #3: Compromises
  To keep the efficiency high, the separated cooling loops have to be short!
  Shortest possible cooling loop: 1 Magnet (15 m)
  For 5500 arc magnets (dipoles and quadrupoles)
  Minimal 16500 Valves, 5500 heat exchangers, 5500 separators, ...
  → Large controlling effort
  → High CAPEX
  → Decreased availibilty
  → Error-prone installations
  Same question/consideration for the level above:
  How many magnets are supplied by the same Cryoplant?
24

## Slide 25
  Lattice Half-Cell
  Long arc (8.4 km)
  QRL
  Cold Mass
  Short arc (4.4 km)
  Cryogenic distribution line
Challenge #3: Compromises
25

## Slide 26: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Challenge # 2: Much power for low temperature
  Challenge # 3: Efficiency vs. Simplicity
  Challenge # 4: As big as possible
  Compromise between the largest available and the smallest acceptable

## Slide 27: Challenge #4: Size matters
Cavern
FCC tunnel
Surface
100 kW @ 4.5 K
  ITER: 25 kW @ 4.5 K
  FCC: 100 kW @ 4.5 K
  x 4

## Slide 28
Challenge #4: Size matters
  60 x Gaseous He (250 m3, 20 bar)
  156 x Quench Buffer (250 m3, 20 bar)
  10 x Gaseous He (250 m3, 50 bar)
  10 x Nelium (250 m3, 50 bar)
  50 x Liquid He (120 m3)
  10 x Gaseous Ne (10 m3, 200 bar)
  6 x Liquid N (50 m3)
  6 x He Boil-off liquefier (150 ÷ 300 l/h)
  Courtesy of CERN
  Courtesy of CERN
  Courtesy of CERN
  Courtesy of CERN
28

## Slide 29: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Challenge # 2: Much power for low temperature
  Challenge # 3: Efficiency vs. Simplicity
  Challenge # 4: As big as possible
  New solutions for old problems
  Challenge # 5: Attempt for new technology

## Slide 30
Challenge #5: Sometimes change a winning team
  Long arc (8.4 km)
  Courtesy of Pawel Duda
  0.64 Fe
  0.36 Ni
  Cool down: 300 K → 60 K
  304L: DL ≈ 28 m
  Invar: DL ≈ 3.5 m
Invar technology for the QRL
Efficiencies of centrifugal compressors higher than for screw compressors
Nelium Brayton Cycle
  → Helium compressors need to be very large due to low density
  Courtesy of MAN
  Nelium is a blend of helium (75 %) and neon (25 %)
Assumed Carnot efficiency 0.42 →
Electrical Power Pel ≈ 9 MW
Cooling Capacity (@ 40 ÷ 300 K):
270 kW @ 40 ÷ 300 K (Cold Mass & Current Leads)
700 kW @ 40 ÷ 63 K (Beam Screen & Thermal Shield)
30

## Slide 31: Challenge #5: Sometimes change a winning team
Cool Down with N2 (80 K)
10 trucks per hour (nonstop)
Nitrogen Storage (60000 m3)
For the same CD timescale (≈ 10 d):
6 x
  Courtesy of CERN
Cool Down with Nelium Cycle (40 K)
Cool Down and Warm Up operations with the Beam Screen Cooling Warm Compressor and the Nelium Cycle
  Courtesy of MAN
  pmax = 20 bar
  pmax = 50 bar
  Courtesy of Hugo Correia Rodrigues

## Slide 32: FCC-hh Cryogenics Challenges
  Challenge # 1: Cryogenics is an ancillary application
  Challenge # 2: Much power for low temperature
  Challenge # 3: Efficiency vs. Simplicity
  Challenge # 4: As big as possible
  Find a solution for 99 % of the machine doesn‘t mean to have solved 99 % of the problems
  Challenge # 5: Attempt for new technology
  Challenge # 6: Little big problems

## Slide 33
Challenge #6: Technodiversity
  Example # 1: Inner Triplet Cooling
  Example # 2: Quenching
35 MJ / Magnet
  Max. allowed pressure 20 bar
  Capacity of header D
  Capacity of quench buffers
  ...
  Example # 3: BSC-Cycle Transient for HiLumi-FCC
  HiLumi-Beam Life Cycle: 4.5 hours
  → Beam Screen Cooling system never reaches steady-state operation
33

## Slide 34: FCC-hh Cryogenics: Overview
 | Cold Mass Cooling | Current Lead Cooling |  | Beam Screen Cooling & Thermal Shiedling
Heat Load | 155 kW | 1.7 kW | 1165 kW | 5980 kW
Temperature level | 2.05 K | 4.5 K | 36 ÷ 300 K | 40 ÷ 62 K
Minimal electrical power (Carnot) | 17500 kW | 112 kW | 1641 kW | 29100 kW
Electrical Power Consumption | 131.5 MW | 6.8 MW |  | 80.3 MW
Overall exergetic efficiency | 0.13 | 0.26 |  | 0.36
Cryopower @ 4.5 K / Cryoplant | 103 kW @ 4.5 K (x 10 Cryoplants) |  |  | 
FCC-hh Cryo Summary
Cryogen Inventory during nominal operation
 | Helium | Neon | Nelium | Nitrogen
Cold Mass | 400 t | - | - | -
Distribution System | 350 t | - | - | -
Cryoplants (+ Shafts) | 8 t | 5 t | 39 t | -
Storage | 88 t | 10 t | 1 t | 242 t
Sum | 846 t | 15 t | 40 t | 242 t

## Slide 35: FCC Cryogenic Challenges: LEP/LHC vs FCC
 | LEP |  | FCC-ee |  |  | 
Research object | z0 | w± | z0 | w± | h | t1 & t2
Number Cryoplants | - | 4 | 1 | 2 | 2 | 4
Total Cryopower [kW @ 4.5 K] | - | 48 | 4 | 41 | 82 | 126
Total Cryopower per cryoplant [kW @ 4.5 K] | - | 12 | 4 | 41 | 41 | 63
LEP vs. FCC-ee
 | HL-LHC | FCC-hh
Number Cryoplants | 10 | 10
Total Cryopower per cryoplant [kW @ 4.5 K] | 18 | 103
Total electric power consumption (w/o IPs) [MW] | 42 | 220
Max. Distribution Distance (long sector) [m] | 3300 | 8400
Overall storage capacity [m3] | 16400 | 65400
Helium inventory [t] | 145 | 846
Neon inventory [t] | 0 | 25
Nitrogen inventory [t] | 40.5 | 242
HL-LHC vs. FCC-hh
Factor 5 ÷ 6
Factor 5 ÷ 6
Factor 5 ÷ 6
Factor 4
Factor 2 ÷ 3
Factor 6 ÷ 7
Factor 6
= 4 x state-of-the-art capacity

## Slide 36: The FCC cryogenic needs
  LHC
  FCC
  SPS
  PS
  LEIR
  Reliability
  Efficiency
  Keep cool heads upon the challenges
Cold-bloodedly calculating Engineers
… and who shall deliver that if not Cryogenics?
Icy determination to make decisions
  Keep chilled in hot discussions

## Slide 37
The cryogenic needs of the FCC
"What starts out as science fiction today may wind up being finished tomorrow as a report.“
Norman Mailer
2019 European Cryogenics Days
08.10.2019 in Lund, Sweden

## Slide 38: A brief overview: The FCC
A
B
C
D
E
F
G
H
I
J
K
L
  Courtesy of J.Osborne
  ≈ 600 m
  Limestone (5 %)
  ?
  ?
  ?
  ?

## Slide 39: A brief overview: The FCC-ee (2038 - 2053)
A
B
C
D
E
F
G
H
I
J
K
L
  Lepton Collider to study 4 particles: z0-Boson, w±-Boson, Higgs Boson, Top Quark
  Two experiments (interaction points) with small cryogenic needs in the Points A & G
  Large cryogenic consumers are the RF Cavities located in the Points D & J (+ distribution)

## Slide 40: A brief overview: The FCC-hh (2064 - 2090)
A
B
C
D
E
F
G
H
I
J
K
L
  Hadron Collider to study massive particles and eventually discover new physics (e.g. SUSY)
  Four experiments (interaction points) and superconducting RF Cavities with small cryogenic needs in the Points A, B, G, H & L
  Large cryogenic consumers are the magnets to bend and focus the hadron beams (+distribution)

## Slide 41: Benefits for the research
 | LEP |  | FCC-ee |  |  |  | 
Research object | z0 | w± | z0 | w± | h | t1 | t2
Particle Energy [GeV] | 60 (max.) | 105 (max.) | 45.6 | 80 | 120 | 175 | 182.5
Beam Current [mA] | 8.4 | 6.2 | 1390 | 147 | 29 | 6.4 | 5.4
Luminosity / IP [nb·s-1] | 0.0085 | 0.025 | 230 | 28 | 8.5 | 1.8 | 1.55
RF voltage [GV] | 0.4 | 4.1 | 0.1 | 0.75 | 2.0 | 4.0 / 5.4 | 4.0 / 6.9
RF frequency [MHz] | 352.2 |  | 400 |  |  | 400 / 800 | 
Lepton Colliders
 | LHC |  | HL-LHC |  | FCC-hh | 
Research object | p+ | Pb | p+ | Pb | p+ | Pb
Nucleon Energy [TeV] | 7 | 1.38 | 7 | 1.38 | 50 | 19.7
Total Beam Energy [MJ] | 392 | 1.9 | 694 | 3.4 | 8300 | 362 ÷ 709
Beam Current [mA] | 584 | < 1 | 1120 | < 1 | 500 | < 1
Luminosity / IP [nb·s-1] | 2.5 | 0.5 · 10-6 | 12.5 | 6 · 10-6 | 12.5 ÷ 75 | 80 · 10-6 ÷ 320 · 10-6
Dipole Field [T] | 8.33 |  |  |  | 16 | 
Hadron Colliders

## Slide 42: FCC-ee Cryogenics: Stage 1/4 (z-Boson)
Beam 2
Beam 1
Booster
QRL
A
B
C
D
E
F
G
H
I
J
K
L
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Number Cryoplants | 1 CP @ Point J | -
RF voltage | 100 MV | -
Cryopower / Cryoplant | 4 kW @ 4.5 K | 
Total Cryopower @ 4.5 K | 4 kW @ 4.5 K | 
Electrical Power | 0.9 MW | 
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)
Frequency | 400 MHz | 800 MHz
Tsat (pSat) | 4.5 K (1.3 bar) | 2.0 K (30 mbar)

## Slide 43: FCC-ee Cryogenics: Stage 2/4 (w-Boson)
Beam 2
Beam 1
Booster
QRL
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Frequency | 400 MHz | 800 MHz
Tsat (pSat) | 4.5 K (1.3 bar) | 2.0 K (30 mbar)
Number Cryoplants | 1 CP @ Point J | -
RF voltage | 750 MV | -
Cryopower / Cryoplant | 41 kW @ 4.5 K | 
Total Cryopower @ 4.5 K | 41 kW @ 4.5 K | 
Electrical Power | 9.5 MW | 
A
B
C
D
E
F
G
H
I
J
K
L
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)

## Slide 44: FCC-ee Cryogenics: Stage 3/4 (Higgs Boson)
A
B
C
D
E
F
G
H
I
J
K
L
Beam 2
Beam 1
Booster
QRL
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Frequency | 400 MHz | 800 MHz
Tsat (pSat) | 4.5 K (1.3 bar) | 2.0 K (30 mbar)
Number Cryoplants | 1 CP @ Point J & D | -
RF voltage | 2000 MV | -
Cryopower / Cryoplant | 41 kW @ 4.5 K | 
Total Cryopower @ 4.5 K | 82 kW @ 4.5 K | 
Electrical Power | 19 MW | 
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)

## Slide 45: FCC-ee Cryogenics: Stage 4/4 (Top Quark)
A
B
C
D
E
F
J
K
L
Beam 1&2
Booster
QRL
Newly installed 400 MHz RF Module @ 4.5 K
Formerly installed 400 MHz RF Module @ 4.5 K
Newly installed 800 MHz RF Module @ 2.0 K
Frequency | 400 MHz | 800 MHz
Tsat (pSat) | 4.5 K (1.3 bar) | 2.0 K (30 mbar)
Number Cryoplants | 2 CPs @ Point J & D | 2 CPs @ Point J & D
RF voltage | 4000 MV | 5400 / 6900 MV
Cryopower / Cryoplant | 41 kW @ 4.5 K & 12 kW @ 2.0 K | 
Total Cryopower @ 4.5 K | 252 kW @ 4.5 K | 
Electrical Power | 58 MW | 
Header A: 800 MHz RF Cavities Supply (2.2 K / 1.3 bar)
Header B: 800 MHz RF Cavities Supply (2.0 K / 30 mbar)
Header C: 400 MHz RF Cavities Supply (4.6 K / 3 bar)
Header D: 400 MHz RF Cavities Return (4.5 K / 1.3 bar)
Header E: Thermal Shields Supply (50 K / 20 bar)
Header F: Thermal Shields Return (75 K / 18 bar)

## Slide 46: FCC-hh Cryogenics: Cold Mass
  Coils
  Collar
  Iron Yoke
  Cold Mass
  Superfluid helium bath
  Bayonet heat exchanger
  Tmax = 2.05 K
  1.44 W/m
  0.24 W/m
QCM | 
QB | 
  Courtesy of CERN
  Courtesy of CERN
Pmin | 
Preal | 
12.1 kW
2 kW
@ 1.8 K
1.8 MW
13 MW
  Values for one long sector:
Cold Mass Cooling

## Slide 47: FCC-hh Cryogenics: Beam Screen & Thermal Shields
  31.1 W/(m·Aperture)
  5.3 W/m
  4 W/m
Pmin | 
Preal | 
@ 40 ÷ 62 K
2.9 MW
8.1 MW
QBS | 
QTS | 
PCirc | 
520 kW
80 kW
100 kW
  Courtesy of CERN
  Beam Screen Cooling Channel (40 ÷ 60 K)
  Values for one long sector:
Beam Screens and Thermal Shields (Baseline)

## Slide 48: FCC-hh Cryogenics: Beam Screen & Thermal Shields
  31.1 W/(m·Aperture)
  5.3 W/m
  4 W/m
Pmin | 
Preal | 
@ 40 ÷ 62 K
2.9 MW
8.7 MW
QBS | 
QTS | 
PCirc | 
520 kW
80 kW
370 kW
  Courtesy of CERN
  Beam Screen Cooling Channel (40 ÷ 60 K)
@ 40 ÷ 300 K
Beam Screens and Thermal Shields (Option)
  Values for one long sector:

## Slide 49
Beam screen cooling and thermal shielding
  Cryogenic distribution line
  FCC dipole
  Beam Screens
  The branched flow is divided and passes 4 cooling channels in 2 beam screens (40 K – 60 K)
  Beam screens works as thermal barriers to shield the cold mass (T < 2 K) against beam induced heat loads
  Heat sources generate a heat load of about 60 W/m on the beam screens in total
  300 K
  60 K
  ≈ 2 K
  p = 50 bar
  T = 40 K
  2 operation temperatures investigated

## Slide 50: FCC-hh Cryogenics: Current Leads
Current Leads
Pmin | 
Preal | 
QCL | 
  170 W
  117 kW
117 kW
175 kW
680 kW
@ 4.5 ÷ 300 K
  Courtesy of CERN
  Values for one long sector:

## Slide 51: FCC-hh Cryogenics: Nelium Cycle
Nelium Brayton Cycle
Baseline: Cool Down and Warm Up operations with the Beam Screen Cooling flow scheme, a Warm Compressor and the Nelium Cycle
Cooling Capacity (@ 40 ÷ 300 K):
700 kW @ 40 ÷ 63 K (Beam Screen & Thermal Shield)
270 kW @ 40 ÷ 300 K (Cold Mass & Current Leads)
Uses a blend of helium (75 %) and neon (25 %)
  → Increased density:
  Higher pressure ratios per stage
  Centrifugal instead of volumetric machine
Cool-Down and Warm-Up Operations

## Slide 52: FCC-hh Cryogenics: Nelium Cycle
Nelium Brayton Cycle
Blend of helium (75 %) and neon (25 %)
  Courtesy of MAN
Courtesy of Steffen Klöppel
Steady-State
Cool-Down
  p
  in
  p
  out
  p
  in
  p
  out
Steady-State