## Slide 1: European Spallation Source TAC-19 Water Cooling Systems
Håkan Carlsson
Group Leader Fluid Systems – Target Division
European Spallation Source ERIC
2019-04-11

## Slide 2: Outline
Overview
Primary Water Cooling Systems
Radiolysis Gas Treatment System
Water Purification
Drainage
Control system & Commissioning

## Slide 3: Overview

## Slide 4: Radiation Safety
Limit external exposure to ionizing radiation:
  this function has to be achieved to prevent external exposure to public and personnel from both prompt radiation and residual radiation,
Limit internal exposure:
  ensuring the personnel, public and the environment are protected against radioactive material releases. This function is achieved with static and dynamic confinement at the process level and/or at the building level and also by controlling the access to the different areas according to their contamination level.
Monitor releases:
  in order to check planned releases and to enable reacting in case of unexpected releases in compliance with GSO [2],
Control heat:
  to avoid confinement failure and associated radioactive releases. Controlling heat source and heat distribution ensures this function by using active and/or passive heat removal systems according to the facility state.
ESS rule

## Slide 5: Main functions of cooling systems
Primary Water Cooling
  Cool the components affected by nuclear heating (4)
  Confine radioactivity (1, 2)
    Closed systems
  Support systems
    Drainage (2)
    Purification (1, 2)
      Purify the water to reduce corrosion
      Reduce activation products in the system
    Radiolysis Treatment – primary cooling systems (1)
      Remove and treat the gases from the systems – mainly hydrogen
    Sampling (3)
Intermediate Cooling
  Cool the primary cooling systems and act as a barrier to Conventional Facility (CF) cooling (1, 2, 4)
  Support systems
    Drainage

## Slide 6: Heat deposition in Monolith Structure
Cooled component | Cooling demands, (kW) | Tin (oC)
Thermal water moderators | 160 | 
Proton Beam Window & Plug | 6 | 
Water Moderator Primary Cooling | 166 | 20
Reflectors | 250 | 
Reflectors Primary Cooling | 250 | 20
Steel shielding | 500 | 
Moderator/Reflector Frame | 650 | 
Target Monitoring Plug | 2 | 
Proton Beam Instrumentation | 5 | 
Neutron Beam Inserts | 16 | 
Proton Beam Window Port Block | 10 | 
Shielding & Plugs Primary Cooling | 1183 | 35
Total | 1599 | 
Target Wheel (Helium Cooled) 3 MW
Moderators/Reflectors
Proton Beam Window
Shielding
Target Monitoring
Proton Beam
Instrumentation Plug
NBI
Target Wheel
Notes: Three water cooling loops
Thermal Moderator + PBW 178 kW
Reflectors + PBW
Shielding & Plugs
5 MW = 9 % mass, 2 % neutronos, 89 % heat 4450 kW

## Slide 7: Target Station - Cooling Systems
A
CUB 8oC
CUB 25oC
CUB 50oC
Intermediate 15oC
Intermediate 30oC
Target Intermediate 55oC
Target Intermediate 30oC
Target Intermediate 30oC
Water Moderators
Shielding & Plugs
Reflectors
Target Helium Cooling
“District Heating”
Primary Cooling Systems
Intermediate
Systems
Central Utility
Block
Monolith
Thermal Moderators
Reflectors
Proton Beam Window
Proton Beam Instrumentation Plug
Monitoring Plug
Shielding
Neutron Beam Inserts
Moderator plug
PBW Port Block
Target Wheel

## Slide 8: Design considerations Primary Water Cooling systems
Safety Analysis done
  Safety Related Systems
  Mechanical Quality Class 4
Radionuclides in the primary water cooling systems
  Confine the water
  Minimize release of radioactive gases to public
  Protect workers from γ-radiation
    All systems in non-accessible rooms during operation
    Minimum 4h before entering after beam stop
    Extra shielding outgoing pipes & delay tanks
    High corrosion resisting material – SS 1.4404 (316L)
    Purify the water to avoid hotspots in components (maintenance)
    Hard-facing in valves must not consist of or be lined with alloys with a cobalt content exceeding 0,20%
  Protect components
    Delay tank
  3H needs to be considered during maintenance (opening up systems)
Hydrogen production – radiolysis process
  Slope of pipes from components in monolith until GLS-tank (no pockets)
  Vent gases (hydrogen) from the systems

## Slide 9: Primary Water Cooling Systems

## Slide 10: Primary Water Cooling System
90s
300s
Considerations
Water activation
  Delay tank
  Non-accessible rooms
Radiolysis
  GLS tanks
  Re-combiner system
Isotope | Half-life | Decay mode | Time step [0s] | Time step [90s]
3H | 12.3 y | β | 621.3 | 621.3
7Be | 53d | ECβ + γ[477keV ] | 445.1 | 445.1
11C | 1223 s | β | 1473 | 1400
14O | 70.6 s | ECβ + γ[2.3MeV ] | 92.3 | 38.5
15O | 122 s | β | 4511 | 2723
16N | 7.1 s | β + γ[6.1MeV ] | 4462 | 0.8
Total |  |  | 12380 | 5657
Total activity in Curies, only isotopes contributing in excess of 10Cu at 60 s cooling are listed
(Esben Klinkby)

## Slide 11: Moderator Primary Water Cooling
P: 166 kW
Tin = 20 oC (to cooled object)
Tut = 29 oC (from cooled object)
Pump
  Redundant
  Magnetic & hermetic
  Flow 22,3 m3/h
  TDH: 44 m
Pressure
  Controlled by frequency converter on pump & pressure transmitter
  All transmitters outside room
Flow
  Flow Control Valves
  Pneumatic controlled

## Slide 12: Reflectors Primary Cooling
P: 250 kW
Tin = 20 oC (to cooled object)
Tut = 49,9 oC (from cooled object
Pumps:
  Redundant
  Magnetic & hermetic
  Flow: 18,4 m3/h
  TDH: 44 m
Pressure
  Controlled by frequency converter on pump & pressure transmitter
  All transmitters outside room
Flow
  Flow Control Valves
  Pneumatic controlled

## Slide 13: Shielding & Plugs Primary Cooling
P: 1183 kW
Tin = 35 oC (to cooled object)
Tut = 49,3 oC (from cooled object
Pumps:
  Redundant
  Magnetic & hermetic
  Flow: 96,4 m3/h
  TDH: 53 m
Pressure
  Controlled by frequency converter on pump & pressure transmitter
  All transmitters outside room
  Pressure switches – hardwired to pump power supply
Flow
  Flow Control Valves
  Pneumatic controlled
  Flow switches (for cooling circuits without flow measurement)

## Slide 14: Shielding & Plugs Primary Cooling

## Slide 15: Primary Water Cooling Systems
Level 115
GLS tanks
Delay tanks
Control Valves
Level 100
Pumps
HX:s
Monlith Vessel
Connection Cell
Connection Cell

## Slide 16: Primary cooling systems inside connection cell
Moderator Reflector
Shielding & Plugs Proton Beam Window
Proton Beam Window
& Proton Beam Window Plug

## Slide 17: P&ID, Shielding & Plugs
Connection Ring
TT
TT
TT
FCV
125
FCV-125
80-16
FT
TP-1043-07
PS
Connection Cell
FS
FS
FS
DN80
DN40
DN40
DN40
DN40
DN40
DN40
DN150
Flow Distribution
Valve
Ball
Valve
Ball
Valve
Ball
Valve
FT = Flow Transmitter
FCV = Flow Control Valve
PS = Pressure Switch
FS = Flow Switch
TT = Temperature Transmitter
Design pressure:
Main Loop = 10 bar (a)
Components = 10 bar (a) or 5 bar (a)
Flow Distribution
Valve
Flow Distribution
Valve

## Slide 18: Pressure Switch (example)
BETA B type

## Slide 19: Flowswitch (example)
Type DW-R

## Slide 20: Temperature Sensor (example)
PT-100

## Slide 21: Shut off valve / Ball valve (example)
Worcester A44
Purpose:
Drain & drying

## Slide 22: Some of the main components
Intermediate Water Cooling Systems
Alfa Laval
Primary Water Cooling Systems
(Alfa Laval – not decided yet)
Magnetic Hermetic Pumps (KSB)

## Slide 23: Radiolysis Gas Treatment System

## Slide 24: Connection to Radiolysis Treatment System

## Slide 25: Radiolysis Gas Treatment System
Radiolysis
Decomposition of water, H2O => H2 + ½ H2O2
Generation of oxygen, H2O2 + radical => H2 + ½ O2 (secondary reaction)
Requirements
Recombine the hydrogen formed
Keeping the concentration of hydrogen below the lower flammability level
Keeping the non re-combinable spallation gases contained until decay
allows release to the atmosphere (11C, 14O, 15O)

## Slide 26: Water Purification System

## Slide 27: Water Purification System

## Slide 28: Water purification – Primary Cooling Systems
2 columns/system
  Fixed columns
  Lead shielded 4 cm
  One running and one standby or decay
Exchange of resin
  At most once/year
  Conductivity > 0,5 𝜇Sm/cm ?
  Transport Vessel
  Mock-up

## Slide 29: Drainage

## Slide 30: Drainage
Re-use the water as much as possible
Seperate vessels for:
All three primary cooling systems
All three intermediate cooling systems
Storage vessels:
  2 x 17 m3 floor drain (sprinkler water)
  1 activated water => waste
  1 non-activated water => waste
Connection to waste ?

## Slide 31: Shielding

## Slide 32: Shielding of Primary Water Cooling Systems
Pipes in connection cell
● No shielding is required downward
● 4 cm lead shielding is required upward
● 8 cm lead shielding is required toward instrument hall
Delay tanks
● 4 cm lead shielding is required downward
● 14 cm lead shielding is required upward
● 14 cm lead shielding is required toward instrument hall
10 t
90 t

## Slide 33: Intermediate Water Cooling Systems

## Slide 34: Target Intermediate Water Cooling
Three independent loops
Heat Exchangers (Alfa Laval)
  1500 kW
  1600 kW
  437 kW
Pumps (KSB magnetic)
  26,1 m3/h
  27,9 m3/h
  27,9 m3/h
Control:
He-temp after HX:s
  Frequency converter
  (Control valve)
Helium
Relief system from water side of He-heat exchangers

## Slide 35: Control system & Commissioning

## Slide 36: Control System design & Commissioning
Target
Specification of function
  State machine concept
  System chains
  Individual systems
  Target Station
Electrical design of automation cabinets
System testing & commissioning
ICS
Implementation of control system
PLC:s
Control room
System testing & commissioning
Responsibility

## Slide 37: Target Systems – System Relations

## Slide 38: Shielding & Plugs Cooling – System relations

## Slide 39: Moderator & Reflector – System relations