## Slide 1: Safety Analysis and Safety Functions
Dr Fan Ye
PSS Safety Engineer, Engineering Safety Consultants Limited (ESC), UK
ESS/ICS/PS
2019-02-11
TS2 PSS Preliminary Design Review

## Slide 2: Contents
TS2 PSS Initiating Events Analysis
TS2 PSS SIL Determination
TS2 PSS SRS
TS2 PSS SIL Verification (preliminary)

## Slide 3: Route map
SRS
SIL Verification
TS2 Risk Assessment
Initiating Events Analysis
SIL Determination

## Slide 4: Route map
SRS
SIL Verification
TS2 Risk Assessment
Initiating Events Analysis
SIL Determination

## Slide 5: TS2 PSS Initiating Events Analysis Hazards requiring PSS
Hazards identified from TS2 Risk Assessment
A subset require protection from PSS
  TS2_HAZ01, Ionising radiation (X-rays)
  TS2_HAZ02, Non-ionising radiation (radio frequency)
  TS2_HAZ03, Oxygen deficiency (ODH)
Lead to a list of overall safety requirements for PSS

## Slide 6: TS2 PSS Initiating Events Analysis Overall safety requirements
Req. ID | Requirement Description
TS2PSS_REQ01 | TS2 bunker shall be searched prior to lock-up and search shall be controlled by PSS.
TS2PSS_REQ02 | TS2 PSS shall prevent access to TS2 bunker area during operation.
TS2PSS_REQ03 | TS2 PSS shall interface the RF waveguide during the Klystron testing outside of the TS2 bunker to ensure that the RF power to CM is disconnected.
TS2PSS_REQ04 | TS2 PSS shall have the interface with radiation monitors outside TS2 bunker area to switch off the RF power in case of high radiation.
TS2PSS_REQ05 | ODH detection system shall be installed outside the TS2 bunker (if the oxygen levels inside the bunker drop below 18% the ODH evacuation alarms shall be triggered).
TS2PSS_REQ06 | TS2 PSS shall provide means within TS2 bunker to switch off the RF power in case of emergency.

## Slide 7: TS2 PSS Initiating Events Analysis IEs
IE ID | Initiating Event Description | Hazard
TS2PSS_IE01 | TS2 operation started inadvertently | TS2_HAZ01, TS2_HAZ02
TS2PSS_IE02 | Intrusion into bunker during TS2 operation | TS2_HAZ01, TS2_HAZ02
TS2PSS_IE03 | failure to remove waveguide prior to Klystron testing | TS2_HAZ01, TS2_HAZ02
TS2PSS_IE04 | equipment failure leading to release of Helium into TS2 bunker | TS2_HAZ03
TS2PSS_IE05 | high radiation from bunker opening | TS2_HAZ01, TS2_HAZ02

## Slide 8: TS2 PSS Initiating Events Analysis IE register
IE ID | IE Description | Hazard ID | Hazard | IE Likelihood | Conseq. | Risk
TS2PSS_IE01 | TS2 operation inadvertently started | TS2_HAZ01 | Ionising radiation | 1.2 per year Justification: 1 CM tested/month Max. 2 weeks (10 days) TS2 op. 1/day TS2 op. 120/year (=1 x 12 x 10 x 1) Human error 1/100 trained personnel following writing procedure, under low level of stress The overall frequency: 1.2 per year | >20mSv / event | Ref. [RA]
 |  | TS2_HAZ02 | Non-ionising radiation |  | Burns | Ref. [RA]

## Slide 9: TS2 PSS Initiating Events Analysis ETA – Intrusion into TS2 bunker
IE: Intrusion into TS2 bunker
TS2 Operation Warning
TS2PSS_SIF04: PAD lock
TS2PSS_SIF02: Intrusion Interlock
Consequence

## Slide 10: TS2 PSS Initiating Events Analysis ETA – Failure to remove waveguide
IE: failure to remove waveguide
Occupancy factor
TS2PSS_SIF05: Waveguide interlock
Consequence

## Slide 11: TS2 PSS Initiating Events Analysis SIFs
SIFs
  TS2PSS_SIF01 Emergency switch-off button
  TS2PSS_SIF02 Intrusion interlock
  TS2PSS_SIF03 Key switch interlock
  TS2PSS_SIF04 Personnel Access Door lock
  TS2PSS_SIF05 Waveguide interlock
  TS2PSS_SIF06 High radiation interlock
SIFs action (except TS2PSS_SIF04)
  Remove permit to energise the TS2 modulator and the LLRF
TS2PSS_SIF04 action
  Electrically lock the personnel access door

## Slide 12: Route map
SRS
SIL Verification
TS2 Risk Assessment
Initiating Events Analysis
SIL Determination

## Slide 13: TS2 PSS SIL Determination Methodology – LOPA
IEC 61511-3
Notes: Figure A.1 illustrates the general concepts of risk reduction. The general model assumes that:
– there is a process and an associated basic process control system (BPCS);
– there are associated human factor issues;
– the safety protection layers features comprise:
• mechanical protection system;
• safety instrumented systems;
• non-SIS instrumented systems;
• mechanical mitigation system.

## Slide 14: TS2 PSS SIL Determination Methodology – LOPA
9. Community Emergency Response
8. Plant Emergency Response
7. Fire & Gas System
6. Physical Containment (Bunds)
5. Physical Protection (Relief Devices )
4. E/E/PE safety-related
3. Alarms & Operator Intervention
2. Basic Process Control System
1. Process
Protection Layers: 1,2,3,4,5
Mitigation Layers: 6,7,8,9

## Slide 15: TS2 PSS SIL Determination Methodology – LOPA
Risk
Risks arising from dangerous failures in the process & in the BPCS
Risk reduction achieved by Conditional Modifiers
Risk reduction achieved by Other Risk Reduction Measures
Risk reduction
achieved by SIS/SIF
Target Risk
F3
Demands

## Slide 16: TS2 PSS SIL Determination Methodology – LOPA
Risk
Risks arising from dangerous failures in the process & in the BPCS
Risk reduction achieved by Conditional Modifiers
Risk reduction achieved by Other Risk Reduction Measures
Target Risk
F3
SILs
4
3
2
1
Demands

## Slide 17: TS2 PSS SIL Determination Results
Low Demand (demands <1/yr) SIFs
High Demand (demands >>1/yr) SIFs
SIF ID | SIF Description | Risk Target (/yr) | PFD Target | SIL Target
TS2PSS_SIF01 | Emergency switch-off | 1.0E-6 | 2.8E-2 | SIL 1
TS2PSS_SIF02 | Intrusion interlock | 1.0E-6 | 1.0E-3 | SIL 2
TS2PSS_SIF05 | Waveguide interlock | 1.0E-6 | 3.3E-5 | SIL 4
TS2PSS_SIF06 | High radiation interlock | 1.0E-6 | TBC | TBC
SIF ID | SIF Description | Risk Target (/hr) | PFH Target | SIL Target
TS2PSS_SIF03 | Key switch interlock | 1.1E-10 | 3.7E-6 | SIL 1
TS2PSS_SIF04 | Personnel access door lock | 1.1E-10 | 1.1E-7 | SIL 2
Notes: SIF05 – IE 0.1/yr, occupancy 30%, no other IPLs; shutter switch, controlled access to bunker, etc.
SIF06 – IE (design issue?? – redesign, limit power, exclusion zone, etc.)

## Slide 18: TS2 PSS Initiating Events Analysis ETA – Failure to remove waveguide (NEW)
Notes: Proposed changes (1 additional layer): shutter switch, control room feedback, independent check, controlled access during RF testing

## Slide 19: TS2 PSS SIL Determination Results – Updated for TS2PSS_SIF05
Low Demand (demands <1/yr) SIFs
High Demand (demands >>1/yr) SIFs
SIF ID | SIF Description | Risk Target (/yr) | PFD Target | SIL Target
TS2PSS_SIF01 | Emergency switch-off | 1.0E-6 | 2.8E-2 | SIL 1
TS2PSS_SIF02 | Intrusion interlock | 1.0E-6 | 1.0E-3 | SIL 2
TS2PSS_SIF05 | Waveguide interlock | 1.0E-6 | 3.3E-5 | SIL 4
 |  | 1.0E-6 | 3.3E-4 | SIL 3
TS2PSS_SIF06 | High radiation interlock | 1.0E-6 | TBC | TBC
SIF ID | SIF Description | Risk Target (/hr) | PFH Target | SIL Target
TS2PSS_SIF03 | Key switch interlock | 1.1E-10 | 3.7E-6 | SIL 1
TS2PSS_SIF04 | Personnel access door lock | 1.1E-10 | 1.1E-7 | SIL 2
Notes: SIF05 – IE 0.1/yr, occupancy 30%, no other IPLs; shutter switch, controlled access to bunker, etc.
SIF06 – IE (design issue?? – redesign, limit power, exclusion zone, etc.)

## Slide 20: Route map
SRS
SIL Verification
TS2 Risk Assessment
Initiating Events Analysis
SIL Determination

## Slide 21: TS2 PSS SRS (ESS-0288460)
Safety Requirements Specification (SRS) for TS2 PSS SIFs
Inputs
  Results from SIL Determination
  Requirements from IEC 61511
  ConOps
Outputs
  SRS (ESS-0288460), used for
    Design and engineering
    SIL Verification (ESS-0478596)
      To confirm the design meet SIL targets from SIL Determination
    Subsequent safety lifecycle stages
      FAT, SAT, commissioning, operation, maintenance, etc.

## Slide 22: Route map
SRS
SIL Verification
TS2 Risk Assessment
Initiating Events Analysis
SIL Determination

## Slide 23: TS2 PSS SIL Verification 1oo1 PLC vs 1oo2 PLCs
Low Demand SIFs
High Demand SIFs
SIF ID | PFD Target | SIL Target | PFD ach’d (1oo1) | Arch. (1oo1) | PFD ach’d (1oo2) | Arch. (1oo2)
TS2PSS_SIF01 (e-switch off) | 2.8E-2 | SIL 1 | 2.0E-4 | SIL 2 | 1.9E-4 | SIL 2
TS2PSS_SIF02 (intrusion) | 1.0E-3 | SIL 2 | 4.9E-5 | SIL 2 | 4.2E-5 | SIL 2
TS2PSS_SIF05 (waveguide) | 3.3E-5 | SIL 4 | 5.9E-4 | SIL 3 | 3.1E-4 | SIL 3
TS2PSS_SIF06 (radiation) | TBC | TBC | TBC | TBC | TBC | TBC
SIF ID | PFH Target | SIL Target | PFH ach’d (1oo1) | Arch. (1oo1) | PFH ach’d (1oo2) | Arch. (1oo2)
TS2PSS_SIF03 (key switch) | 3.7E-6 | SIL 1 | 2.5E-8 | SIL 2 | 2.4E-8 | SIL 2
TS2PSS_SIF04 (door lock) | 1.1E-7 | SIL 2 | 1.1E-7 | SIL 2 | 1.1E-7 | SIL 2

## Slide 24: Questions?
Thank you for your attention!

## Slide 25: Backup slides
Notes: Proposed changes (1 additional layer): shutter switch, control room feedback, independent check, controlled access during RF testing

## Slide 26: TS2 PSS Initiating Events Analysis (ESS-0468688)
Inputs
  TS2 Risk Assessment (ESS-0488867) (hazard identification and analysis)
  TS2 PSS Concepts of Operations (ConOps) (ESS-0304995)
  TS2 PSS Assumptions and Technical Details (ESS-0508222)
Outputs
  List of initiating events (IEs) and associated hazards requiring PSS protection, and their frequencies
  List of high level safety requirements for TS2 PSS
  List of TS2 PSS safety functions (SIFs in IEC 61511 terms)

## Slide 27: TS2 PSS SIL Determination (ESS-0288441)
Safety Integrity Level determination for TS2 PSS SIFs
Inputs
  TS2 PSS Initiating Events Analysis (ESS-0468688):
    list of SIFs
    list of IEs and frequencies
  List of Independent Protection Layers (IPLs)
    ConOps
    Assumptions and Technical Details
Outputs
  SIL targets for SIFs
  Safety Requirements Specification (SRS) (ESS-0288460)

## Slide 28: TS2 PSS SIL Verification (ESS-0478596)
To verify that the design meets the SIL targets
Inputs
  SIL Determination (ESS-0288441) results
Outputs
  SIL Verification (ESS-0478596)
  Updated SRS (ESS-0288460) with SIL Verification results
Method
  Fault Tree Analysis (FTA)
  Reliability Block Diagram (RBD)

## Slide 29: TS2 PSS Initiating Events Analysis ETA – TS2 operation inadvertently started

## Slide 30: TS2 PSS Initiating Events Analysis ETA – ODH

## Slide 31: TS2 PSS SIL Verification RBDs
TS2PSS_SIF01, emergency switch-off button
TS2PSS_SIF02, intrusion interlock

## Slide 32: TS2 PSS SIL Verification RBDs
TS2PSS_SIF03, key switch interlock
TS2PSS_SIF04, personnel access door lock

## Slide 33: TS2 PSS SIL Verification RBDs
TS2PSS_SIF05, waveguide interlock
TS2PSS_SIF06, high radiation interlock