## Slide 1: PSS verification and validation
Paulina Skog On behalf of Protection Systems Group
ESS/ICS/PS
2019-04-09
TS2 PSS Critical Design Review

## Slide 2: Tests

## Slide 3: Agenda
Tests
  Measures and techniques
  Location
  Roles and responsibilities
  Identified items to be verified
  Test documentation
  Correctness of data and adequacy
  Non-conformance and procedures for corrective actions on failure during test
  Tools

## Slide 4: Hardware Factory Acceptance Test (HWFAT)
The TS2 PSS HWFAT will take place at ESS site (Gallery Technical Area) in cooperation between vendor (Processkontroll AB (Actemium)) and PSS team.
The HWFAT verifies that the as-built hardware system (cabinets) meets the specified design.

## Slide 5: Measures and techniques for HWFAT
Tests covering the (IEC 60204-1, Safety of machinery - Electrical equipment of machines - Part 1: General requirements):
  checking functions covering:
    The electric supply
    PLC test of digital inputs
    PLC test of digital outputs
    PLC test of analog inputs
  electrical equipment compliance with the TS2 PSS Electrical and Mechanical Drawings
  checking insulation resistance
  checking disruptive discharge
  checking for residual voltages
  checking if the conditions for protection against indirect contact by automatic disconnection are fulfilled

## Slide 6: Tools for FAT and SAT
Flexible measurement probes
Windows station with TIA portal installed (v 14 SP1 or higher)
FLUKE 1507 Insulation Tester
FLUKE 705 Current Loop Calibrator 24mA

## Slide 7: Roles and responsibilities for HWFAT
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | Hardware designer | Alberto Toral Diez | The hardware designer will support the verifier during testing
Verifier | Hardware verifier | Morteza Mansouri / Peter Holgersson | The hardware verifier will organize the test, conducts the test, ensure that the test report documentation is completed and signed correctly
Role | Company | Name | Function
Vendor representative | Processkontroll AB (Actemium) Organisation number: 556781-1400 | Per Persson | The vendor representative will support the test with the PSS representatives

## Slide 8: Identification of items to be verified for HW FAT
The requirements listed to be verified during the HWFAT in the Hardware Requirements Specifications for Test Stand 2 Personnel Safety System

## Slide 9: Test documentation
For the FAT the following documents will be produced:
Factory Acceptance Test Specification for Test Stand 2 Personnel Safety Systems
Factory Acceptance Test Report for Test Stand 2 Personnel Safety Systems
Note:
These documents will be written after the CDR and will be reviewed during the TRR
All of the tests will have a specification and a test report and all of them will be reviewed during the TRR

## Slide 10: Correctness of data and adequacy
PSS have review procedures to demonstrate the adequacy of the outputs and to verify the correctness of the data produced.
Design and requirement documents are reviewed:
  internally by PSS
  during the CDR by non-PSS experts
  during the Functional Safety Assessment (FSA) by ZHAW.
The test specifications and test reports will be reviewed during the TRR and the FSA.

## Slide 11: Non-conformance and procedures for corrective actions on failure during test
Open items will be identified and listed in a HWFAT punch list and will follow the recommendation in
“ESS Guideline for Factory Acceptance Test (FAT) and Site Acceptance Test (SAT) (ESS-0094204), Rev. 2”
Note the items that cannot be cleared on the spot, will be documented in a non conformity report!
Notes: To be cleared on the spot, HWFAT to continue after rectification
On-going rectification during HWFAT
HWFAT to be repeated
Modifications to be made after HWFAT
Remaining work to be rectified

## Slide 12: Hardware Site Acceptance Test (HWFAT)
The Hardware SAT verifies that the hardware is installed as specified in electrical and mechanical design drawing document.
Hardware SAT include the same tests as the Hardware FAT and some additional field device loop tests and bunker interface test.
Location: The SAT will be performed at ESS in the Gallery Technical Area.

## Slide 13: Roles and responsibilities for FAT
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | Installation coordinator | Mattias Eriksson | The system installation coordinator will support the verifier during testing
Verifier | Hardware verifier | Joakim Söder / Morteza Mansouri | The hardware verifier will organize the test, conducts the test, ensure that the test report documentation is completed and signed correctly

## Slide 14: Identification of items to be verified
The requirements listed to be verified during the HWSAT in the Hardware Requirements Specifications for Test Stand 2 Personnel Safety System
The bunker interface will be tested during this test

## Slide 15: Software Pre-FAT
The Software Pre-FAT verifies the software functionality through simulations.
Software code review to reveal potential software design defects and avoid systematic failures.
Location: The Software Pre-FAT will be performed in the PSS Lab at ESS.

## Slide 16: Measures and techniques for pre-FAT
Simulation
CDR with design walkthrough.
Code review
  Code, configurable hardware and firmware inspections to ensure compliance with software planning document and Software Pre-FAT checklist, which includes structural tests

## Slide 17: Tools for pre-FAT
Windows station with Siemens TIA portal installed (v 14 SP1 or higher), including the safety advanced optional package, WinCC Comfort and PLC Sim, WinCC runtime.
Test environment PLCs and HMIs.
Versiondog installed on the Windows station

## Slide 18: Roles and responsibilities for pre-FAT
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | Software developer | Denis Paulic | The designer will support the verifier during testing
Verifier | Software verifier | Sam Crossland | The software verifier will organize the test, ensure that the test specification is carried out, ensure that the documentation is completed and signed correctly
Reviewer | Software developer | Martin Carroll / Johannes Gustafsson | The reviewer will conduct a code review, for details see the Verification and Validation Plan for Personnel Safety Systems [3]

## Slide 19: Identification of items to be verified
The requirements listed to be verified during the Software Pre-FAT in the Software Requirements Specification for Test Stand 2 Personnel Safety System (SWRS) .
Fully verified:
  Software quality check requirements
  Important software variables to store alarm, error, fault and start-up conditions.
  How sensors and actuators shall be connected (or read) in the software and requirements on I/O modules to which they are connected.

## Slide 20: Identification of items to be verified
Partly verified using simulation:
System interfaces
    Simulation of signals sent to and received from the defined interfaces for the following interfaces:
      RF system
      Radiation monitors
Operator interfaces
      HMI simulation
      Simulating the variables used for interfacing with EPICS
Procedures
      Simulation of formalised search procedure
TS2 ODH detection system alarming
PSS modes of operation (state machine simulation)
Safety Instrumented Functions (SIF)

## Slide 21: Site Integration Test (SIT)
The SIT verifies that installed hardware and software work together properly, ensuring that their combination is serving the purpose of PSS safety functions and procedures.
Note: To reduce the risk of damaging the Stakeholder Associated Equipment (SAE) due to repeated tests, the SAE are not connected to PSS during PSS SIT (Low-Level RF (LLRF) and the modulator)
Location: The SIT will be performed on ESS in the Gallery Technical Area.
Notes: SAE are the equipment in TS2 that TS2 PSS interlocks in order to mitigate risks associated with them (Low-Level RF (LLRF) and the modulator).

## Slide 22: Measures and techniques for SIT
Positive and negative integration tests covering the following:
Interfaces
  RF system
  Radiation monitors
  EPICS
Procedures
  Formalised search procedure
  ODH detection system

## Slide 23: Roles and responsibilities for SIT
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | Software developer | Denis Paulic | The software developer will support the system integrator during testing
Verifier | System Integrator | Morteza Mansouri | The system integrator will organize the test, conduct the test, ensure that the test report documentation is completed and signed correctly
Role | Department and group | Name | Function
Supporting function | Control System Hardware & Integration Support Group | Krisztian Löki | Supporting function for EPICS tests

## Slide 24: Identification of items to be verified
Requirement documents
The safety requirements and SIFs specified in the Safety Requirements Specification for Test Stand 2 Personnel Safety System
The requirements listed to be verified during the SIT in the Hardware Requirements Specifications for Test Stand 2 Personnel Safety System
The requirements listed to be verified during the SIT in the Software Requirements Specification for Test Stand 2 Personnel Safety System (SWRS)
The following areas can be verified.
  TS2 PSS interface with EPICS
  TS2 PSS interface with (Radiological & Environmental Monitoring System) REMS
  Formalised search procedure
  TS2 PSS ODH detection system alarming
  The SIF’s will be partly verified, since the LLRF and the modulator will not be connected during the SIT. The requirements and the SIF ‘s that are not fully verified shall be verified during the FIT.

## Slide 25: Final Integration Test (FIT)
The FIT is a repetition of the positive tests during the SIT, whilst the LLRF and the modulator are operational and connected to PSS.
Location: The SIT will be performed on ESS in the Gallery Technical Area.

## Slide 26: Measures and techniques for FIT
Positive integration tests covering the following:
The SIFs
Interfaces
  RF system
  Radiation monitors
  EPICS

## Slide 27: Roles and responsibilities for FIT
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | Software developer | Denis Paulic | The software developer will support the system integrator during testing
Verifier | System Integrator | Morteza Mansouri | The system integrator will organize the test, conducts the test, ensure that the test report documentation is completed and signed correctly

## Slide 28: Roles and responsibilities for FIT
Role | Department and group | Name | Function
Head of Environment, Safety and Health | ES&H | Peter Jacobsson | Provide PSS with an approval for conducting the FIT
System owner (per section) | Utilities and Test Stands Section | Wolfgang Hees | Provide PSS with an approval for conducting the FIT
Sub system owner 1 (per system) | Control System Hardware & Integration Support Group | Krisztian Löki | Support function for tests covering the EPICS interface
Sub system owner 2 | RF Sources Section | Morten Rostrup Forup Jensen | Support function for tests covering the RF system interface
Sub system owner 3 | Power Converters Section | Carlos De Almeida Martins | Support function for tests covering the modulator interface.
Sub system owner 4 | Radiation Protection Group | Alasdair Day | Support function for tests covering the REMS
Supporting function | Utilities and Test Stands Section | Owen Buchan | Support function for electrical power

## Slide 29: Identification of items to be verified
The safety requirements and SIFs specified in the Safety Requirements Specification for Test Stand 2 Personnel Safety System
The requirements listed to be verified during the FIT in the Hardware Requirements Specifications for Test Stand 2 Personnel Safety System
The requirements listed to be verified during the FIT in the Software Requirements Specification for Test Stand 2 Personnel Safety System (SWRS)
TS2 PSS interface with the modulator
TS2 PSS interface with the RF system
SIF’s

## Slide 30: Validation and handover
To prove that PSS meets the safety and operational requirements, a demonstration of TS2 PSS operation and SIFs shall be presented to all identified stakeholders.
The demonstration shall be carried out on the real system at the ESS site and cover the positive tests from the FIT.

## Slide 31: Roles and responsibilities for validation and handover
 | Role | Name | Function
Manager | Work package manager | Stuart Birch | The work package manager will ensure that the tests are carried out correctly
Designer | System integrator | Morteza Mansouri | The system integrator will organize the test, supports validator in conducting the validation, ensures that the test report documentation is completed and signed correctly

## Slide 32: Roles and responsibilities for validation and handover
Role | Department and group | Name | Function
Technical director or their delegates | Machine Directorate | Roland Garoby | Will witness the validation and approve the handover to operation by signing the validation and handover report.
Associate Director Environment, Safety, Health & Quality or their delegates | ES&H | Ralf Trant | Will witness the validation and approve the handover to operation by signing the validation and handover report.
System owner and validator | Utilities and Test Stands Section | Wolfgang Hees | Validate the system as an operator
Sub system owner 1 (per system) | Control System Hardware & Integration Support Group | Krisztian Löki | Support function for tests covering the EPICS interface
Sub system owner 2 | RF Sources Section | Morten Rostrup Forup Jensen | Support function for tests covering the RF system interface
Sub system owner 3 | Power Converters Section | Carlos De Almeida Martins | Support function for tests covering the modulator interface.
Sub system owner 4 | Radiation Protection Group | Alasdair Day | Support function for tests covering the REMS
Supporting function | Utilities and Test Stands Section | Owen Buchan | Support function for electrical power

## Slide 33: Questions?
Thank you for your attention!