## Slide 1: TS2 PSS Electrical and mechanical design
Critical Design Review
Alberto Toral Diez
Notes: The purpose of this presentation is to give an overview about the hardware detail design for TS2 PSS

## Slide 2: Applicable Standards and regulations
TS2 PSS is a low- voltage protection and monitoring system:
  ESS-0015433, ESS Rules for electrical design 2019
  SS-4364000, Swedish standard for Low-voltage electrical installations
  SS-EN 60204-1, Safety of machinery - Electrical equipment of machines
  IEC 61511, Safety instrumented systems for the process industry sector
Notes: ESS Rules for electrical design, revision of 2019
For the installation, the Low voltage Swedish standard
Safety of machinery for the equipment or cabinets
61511 Functional Safety Standard

## Slide 3: TS2 PSS cabinets location in KG-GTA
PLC Cabinet
Key Exchange Cabinet
Notes: TS2 PSS has two electrical cabinets. The PLC cabinet and the Key Exchange cabinet. The cabinets are located in the rack row 10 and a divider is installed between them, also each cabinet has key lock system coded differently between them

## Slide 4: TS2 PSS cabinet design
  Manufacturer:
  NVENT/SCHROFF
  Dimensions:
  WHD 600x2200x1000 mm
  Variant:
  Varistar EMC cabinet, floor standing
  Double-door, color RAL2000
  IP 55 rating (IEC 60529)
Notes: Double door enclosure that meets the EMC requiremetns

## Slide 5: TS2 PSS PLC cabinet design
  Front door has no perforation.
  Rear door is perforated in the bottom half and has a dust filter
  Rear door has the 15" HMI installed in the top half
  Both doors are equipped with ASSA cylinder and key system

## Slide 6: TS2 PSS PLC cabinet design
  WE1
  Protective Earth Bonding Busbar.
  WE2
  Functional Earth Bonding Busbar.

## Slide 7: PLC cabinet equipotential earth overview

## Slide 8: TS2 PSS PLC cabinet design
  WE1 – (PE)
  Protective Earth Bonding Busbar.
  WE2 – (FB)
  Functional Earth Bonding Busbar.
Rear view

## Slide 9: Symbols information

## Slide 10: Symbols information

## Slide 11: TS2 PSS PLC cabinet design
  The cabinet is air cooled. The top plate has a 3 fans installed that extract the air from the cabinet.
Rear view

## Slide 13: TS2 PSS PLC cabinet design
  Rear mounting plate contains:
  Power arrival terminals
  Switch disconnectors
  MCB’s
  RCD and 2 power socket outlets
  SPD (surge arrester type 3)
  SIEMENS Selectivity modules
  24V DC Potential distributors
  Terminal blocks

## Slide 14: TS2 PSS PLC cabinet design
  230V AC is only present in the first top row from the Rear mounting plate

## Slide 15: TS2 PSS PLC cabinet design
  Front mounting plate contains:
  Network patch panel
  PLC hardware:
    - CPU’s, Communication Processor, Communication Module, SCALANCE Switch, ET200SP interface module and I/O modules
  Power supply, UPS controller and battery unit.
  Relays 3W, 24V DC (48 units)

## Slide 16: TS2 PSS PLC cabinet design
Notes: Main power arrival terminals // Then Disconnector Switch // Surge Protection Device

## Slide 17: TS2 PSS PLC cabinet design
Notes: Power Supply // internal Battery // UPS controller. Is a temporary solution in the future the cabinets will be powered by external UPS power

## Slide 18: TS2 PSS Key Exchange cabinet design
Note: Each key in the key exchange system is uniquely coded
Rear view
Front view

## Slide 19: TS2 PSS Key Exchange cabinet design
Note: The Key Switch is suitable for isolation or switching current
Front view
Key Switch
Key

## Slide 21: Identification of conductors by colour
Notes: As I said before… 60204

## Slide 22: Single core conductors
Earth: GREEN-AND-YELLOW  EN-SS 60204-1 clause 13.2.2
Neutral: LIGHT BLUE  EN-SS 60204-1 clause 13.2.3
AC Power circuits, DC Power circuits exceeding 50V: BLACK

## Slide 23: Single core conductors
DC Control circuits, DC Power circuits below 50V: DARK BLUE
Analog Control circuits: VIOLET
Excepted circuits: ORANGE  EN-SS 60204-1 clause 13.2.4 in accordance with 5.3.5

## Slide 24: PLC hardware
TS2 PSS is a single-train system comprised of.
  Siemens S7-1500 series safety PLC (main CPU):
  CP for connection to PSS engineering Workstation via industrial Ethernet:

## Slide 25: PLC hardware
  Siemens S7-1500 series standard PLC (gateway CPU):
  Communication module 1542-1 for connection to Technical Network via PROFINET (EPICS interface):

## Slide 26: PLC hardware
  ET 200SP, PROFINET Interface-Module + I/O Modules:
  HMI TP1500 Comfort, for touch operation, 15" widescreen:

## Slide 27: PLC hardware
  Uninterrupted Power supply UPS1600 10 A with PROFINET:
  SCALANCE Switch XC206-2SFP manageable layer:

## Slide 28: Network Physical Topology

## Slide 29: PLC modules overview

## Slide 30: PLC I/O modules overview
Inputs:
  53 Fail-safe Digital Inputs
  41 Standard Digital Inputs
  2 Analog Inputs
Outputs
  6 Fail-safe Digital Outputs
  41 Standard Digital Outputs

## Slide 31: TS2 PSS cables overview
Signal cables used for field devices inside TS2 Bunker are HUBER+SUHNER, RADOX 125:
  Radiation resistant, (up to 1000 kGy)
  High temperature (up to 125 °C)
  Low frequency
  Flexible
  Overall screen to mitigate the EMI effect
Other cables types are used where in non-radiation areas: Unitronic® LiHCH and ÖLFLEX® CLASSIC 135 CH

## Slide 32: TS2 PSS multicore cables overview
56 cables in total:
  11 cables for interfaces with other systems,
  (Radio-Frequency, Radiation Monitoring and Fire Alarm)
  37 cables for connection to the PSS Field Devices,
  (including ODHDS)
  8 cables for the Blue/Red lighting system

## Slide 33: Graphical cable diagram reports

## Slide 34: Cable containment system
Legrand Salamandre distribution trunking
Stainless steel conduits
16x1mm Stainless Steel cable conduit. | Part No. 33-004
22x1.5 mm Stainless Steel cable conduit. | Part No. 33-007

## Slide 35
Cable containment system

## Slide 36: Cable containment system
Notes: PAD

## Slide 37: Field Devices: PAD Fortress Mechanical Lock
Spring locked (power to unlock)
Escape release from inside (mechanical push button to release door)
A special key to unlock the unit from outside (to be used by authorized personnel in case of emergency)

## Slide 38: Field Devices: PAD Fortress Mechanical Lock
Notes: Wiring layout for Fortress ProLok with INDEPENDENT safety circuits

## Slide 39: Field Devices: MAD Key-bolt
Opening and closing the MAD is incorporated into TS2 PSS key exchange procedures, by installing a Fortress DM lock on the MAD, which is a simple mechanical solution to lock the MAD without the need for wiring.
Fortress part number DM1-CLSI-A.
Notes: Material Access Door

## Slide 40: Field devices: Non-contact magnetically operated safety switches
A magnetically operated switch comprises a coded switching magnet and a contact block (sensor unit).
Features:
  Tamper-proof protective door monitoring
  Small footprint
  SIL 3 acc. to IEC 61508, achievable with single switch pair
Notes: PSS has DIVERSITY in the position switches on each entry door there is one magnetical switch and one mechanical.

## Slide 41: Field Devices: Mechanical Safety Switches with Separate Actuator
The NC contacts of the switch are forced open mechanically, positively-driven and reliably by the plunger.
An internal mechanism forcibly separates normally closed contacts and prevents them from welding together - allowing the safety circuit to open.

## Slide 42: Field devices: signaling columns
Search Buzzer
Safe state (Green LED)
Search status (White LED)

## Slide 43: Field devices: Emergency Switch-Off Stations
Search Buzzer
Search status (White LED)
Search button
Emergency Switch Off Button
Note: Box painted in Orange RAL2000

## Slide 44: Field devices: information panels
Lasermet LED information panels are installed outside the TS2 Bunker entrances
24V DC powered (0,7 to 1A) with dimming option
Dimensions:
WHD 470x540x63.2mm
Notes: ACCESS/NO ACCESS

## Slide 45
Notes: “ACCESS” and “NO ACCESS”
“RF ON”
“SEARCHING”

## Slide 46: Field Devices: Oxigraf O2iM – High Flow Single port
O2iM oxygen deficiency monitor. The Oxigraf sensor uses laser diode absorption technology to measure oxygen concentration in the gas sample.
The O2iM measures and displays the oxygen concentration in a gas sample drawn through the instrument. Gas is pumped sequentially from the input sample port, through the oxygen sample cell, and out the exhaust port.

## Slide 48: Field Devices: Alarm Plates
Comprised of:
  A red flashing light. Solex xenon from Eaton. Part number: 531024FULL-0088.
  An audible alarm. Multi-tone sounder from Werma. Part number: 14015050
The flashing lights and sounders will turn on when there is Oxygen Deficiency Hazard (ODH)
Notes: ODH when O2 level is below 18%

## Slide 49: Blue and red fluorescent lighting system
A total of four blue and red lights are installed in TS2 PSS controlled areas.
The BLUE lights will turn on when the TS2 PSS permit to RF system is enabled
The RED lights will turn on when there is Oxygen Deficiency Hazard (ODH)
Power: 230V AC, 134W
GLAMOX Part Number: MIR089463

## Slide 50: Blue/Red lights contactor cabinet

## Slide 51: Blue/Red fluorescent lighting system

## Slide 52
Thank you,
any questions?