## Slide 1: Instruments Main Electrical Power Distribution Panel - Specifications and input from Instruments teams –
Markus Larsson, Thomas Gahl
Motion Control & Automation
European Spallation Source ERIC
IKON 17, Lund, 11th September 2019

## Slide 2: Overview
Instruments power distribution
  Interfaces & Responsibilities
  Concept
  Cave Zone
  Test & Measurement
Main Power Distribution Panel
  Generic Requirements NSS
Specifications NSS
  Mechanics
  Components
  Test & Measurements
  UPS
Required input from Instruments teams
Next steps

## Slide 3: Electrical power distribution
Interfaces & Responsibilities
Power distribution is part of the ESS infrastructure and strongly linked to CF, Swedish installation rules etc.
NSS will take over to coordinate, design, deliver and document the power distribution for all instruments including connection to the substation, control racks and any other loads.
This fulfills SSM requirements to be able to track the whole chain from the supply of electricity to the end consumer in a consistent way.
Substation, Main Switch Gear
Instruments power distribution panels
Instruments control racks
CF
NSS
Instruments teams

## Slide 4: Electrical power distribution
Concept
Switchgear breaker 160A (var.)
Substation A
Instrument
Distribution Panel
# 1
# 2
# 3
# 4
# n
Motion
Vacuum
Detector
SE
Light, Hutch
Main Power Panel – Cave Zone
# 1
# 2
# 3
Motion
Chopper
Vacuum
Main Power Panel – Intermediate Zone
# 1
# 2
# 3
Motion
Chopper
Vacuum
Main Power Panel – Bunker Zone
Switchgear breaker 160A (var.)
Substation B

## Slide 5: Electrical power distribution
Cave zone
Sub- Distribution box
Detector rack
Motion Control rack
Vacuum / Utilities Controller rack
PSS rack
UPS
SE Box1
SE Box2
SE Box3
Cave
Control Hutch
Instruments Lab
(Sample Preparation)
230V, 1Ph.
Light
230V, 1Ph.
IT rack
(ICS)
SE Box1
SE Box2
SE Box3
HVAC
Crane
Light
From Sub-station
Chopper rack
UPS
Light
Main Distribution
cabinet
UPS

## Slide 6: Electrical power distribution
Measuring & Monitoring
Voltage and current measurements
  Monitor and analyse L1, L2, L3 and N voltages and currents, calculate power consumption + factor (cos phi)
  Alarm/warnings when outside specified range
Residual Current Monitoring (RCM)
  Isolation of the different grounding zones is calling for a monitoring of the residual currents inside a zone.
  Comparison of L1+L2+L3+N (RCM1) with current to ground on PE (RCM2) gives an indication whether residual currents come from inside or outside an instruments zone.
Data logging + representation in EPICS/NICOS
  Logging and time stamping (short term/long term) of all measured values and analysed results, transfer of the data to EPICS and (selective) to Instrument user screen.

## Slide 7: Main Power Distribution Panel
Generic requirements and resulting design rules from NSS
One main power distribution panel per instrument zone
Avoid magnetic fields and subsequent induction into conductors by keeping L and N as close together as possible in the distribution panels
  Use of MCB with L+N breaking
  Always cable L + N together in the panel, twist L+N wires before installation
  The panel shall be in a metallic housing
Surge protection is needed to protect against overvoltages
  The panel shall be equipped with overvoltage (surge) protection class 2
Measurements and monitoring
  Each instruments main distribution panel shall have a monitoring unit for mains analysis and measuring ground leakage currents
Use of UPS
  The UPS build in the Main Power Distribution Panel shall supply the PSS system and one socket in each of the SE distribution boxes
  Chopper and Detectors will have their own UPS systems.

## Slide 8: Main Power Distribution Panel
Specifications NSS - Mechanical
Mechanics:
  Steel cabinet, RITTAL VX25 series
  H 2000 (+200) x W 800 x D 400
  2 front doors
  200mm plinth
  Input and output cables top or bottom
  Cooling system: TBD
Areas of installation:
  Circuit breaker distribution
  Grounding bar (ZEP)
  UPS
  Diagnostics (in the door)

## Slide 9: Main Power Distribution Panel
Specifications NSS - Standard components
RCBO:
Combination of MCB with RCB/RCCD
Main switch
Surge
protection
All breakers with L+N breaking
MCB:
1+N and 3+N breakers

## Slide 10: Main Power Distribution Panel
Measurement and Data logging of:
  Residual currents
  Harmonics voltage and current
  Flicker
  Under / over voltage + current
  Short voltage drops
  Distortion factor voltage / current
  Transients
  Min / Max
  Unbalance
  power consumption (cos phi...)
Equipment
  Janitza UMG 512 Pro, Graphical Display, GUI
  4 current transducers (64 Amps)
  2 residual current transformers
Specifications NSS – Measuring & Monitoring

## Slide 11: Main Power Distribution Panel
UPS for Chopper and Detectors are integral part of the respective racks
UPS inside Main Power Distribution Panel shall supply 1Phase (230V) to:
  PSS rack (max. 1kW)
  Sample environment box 3 in Cave (1 x 230V socket, max. 1kW, with B6A MCB)
  Sample environment box 3 in Sample Preparation Area (1 x 230V socket, max. 1kW, with B6A MCB)
Specification for UPS:
  Input/Output 1 phase, 230V
  Max. output power 4kW
  Short circuit current capability to trip one B6A circuit breaker (boost function?)
  Run time 15min (@ 3kW)
  Shall work when input is disconnected from both, L and N.
  Working mode: online, double conversion
  Input power factor near to 1
  Output power factor 1
Specifications NSS – UPS

## Slide 12: Main Power Distribution Panel
Specific requirements – Input from the instruments teams
# | Input from instruments team | NSS design goals
1 | List of power consumers in the instrument (type of loads, duty cycle, phases, power, EMC, UPS powered etc.) | Number of circuits/outputs + circuit breakers, Output cable sizes
 |  | Total power of the distribution
 |  | Size of supply cable Size of main switch
2 | Position of the power distribution panel (3D instrument drawing), position of supply cable in the cabinet | Main supply cable routing + raceways Cable length, size of supply cable
 |  | Power calculations
3 | Position of consumers in the instrument zone, distance to the main power panel | Cable routings for supply + raceways Cable length, size of cables
 |  | Position and order of outlets in the cabinet Order of circuit breakers and cabling in the panel

## Slide 13: Next steps
Finish pilot project by defining and delivering latest version of Lab Power Distribution Panels for D04 and D08.
Design and production of prototype for Instruments Main Power Distribution Panel
Review distribution boxes for sample environment
Finalise UPS concept
Start to collect information from Instruments team for load lists

## Slide 14: Thanks!

## Slide 15: Electrical integration
Interfaces
15
Instrument
Engineers
Instruments
Electrical
Integration
Engineer
Motion Control
Design
Chopper Control
Design
Detector Control
Design
Sample environment
Control Design
Load
Amount of cabinets
Cabling
E-plan
Cabinets distribution
Internal Electrical installation: (Lights,
hutch, crane, hutch, hvac, etc)
NSS
Electrical
Integration
Engineer
Load list
Cable list
Cable containments
E3D
Cabinet location
E-plan
Power
Panel Design
E-PLAN
Power Distribution
E-PLAN
Power panel
Design
Grounding template
Template Projects
Grounding Zones
Instrument
NSS
CF
ICS
Power supply
Grounding
Routing in galleries
Sprinkler
Fire sensors
HVAC?
Controls network
E&IS
ePlan
HW Standardisation
ES&H
Electrical safety
CE marking