## First Sheet
TSS probabilistic safety assessment - Appendix I
|  | Name | Role/Title
| Owner | Atefeh Sadeghzadeh | Control engineer, Target Control
| Reviewer | Mikael Olsson | Control engineer, Target Control
| Reviewer | Thomas Hansson | Senior radiation safety engineer, ES&H Division
| Approver | Linda Coney | Group Leader, Target Control

## Instruction
Instruction for Chess Controlled Core Excel Template
(This sheet can be removed when no longer used!)
Document identification and properties
This template is designed for controlled documents being managed in Enovia. Headers and footers may not be edited since these contain attribute information from Enovia that will be automatically populated into the document. The correct methods for updating this information is to save and check-in the document, make the relevant update of document properties in Enovia and then check-out or download the document from the system. Macros must be enabled to allow this synchronisation to occur.
The document title from Enovia can be displayed in any cell by the use of the function “=FirstPrint”. This function is now added on "First sheet".
Master template
The template can be used for creating documents directly or to create new derived templates from which documents can be created. In order to include any new such templates in Chess the procedure ESS-0028581 should be followed.
Layout and sheets
The user may freely change the page layout and size as appropriate for the purpose. Unused sheets may be deleted, although for controlled documents there must always be one sheet with header/footer information corresponding to the “First sheet” in this template. That sheet should always be the left-most sheet since different attributes will be synchronised for this sheet and the other sheets respectively. All sheets can be re-named to reflect their content and new sheets can be added.
Page numbering
When working with a document in view “Page layout” Excel always number all pages internally within each sheet respectively. Printing an individual sheet will result in the same page numbers being printed.
By marking all sheets before making a printout the page numbers will be in one common series including all sheets. Similarly Enovia will during automatic rendering to PDF format arrange all pages in one common page number series for each Excel file

## IEC508 for sensor+transmitter
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0)
MRT=8hours
T1=1 year=8760 hours
2.2789e-06
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 | Lambda extracted from PLC system total (B=20%) | 1.0298e-06
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book | Lambda extracted from relay system total (B=20%) | 1.0464e-06
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 2.7689e-05 | [5 empty] | 0.00219 |  |  | Lambda for sensor subsystem switch | 5.1418e-07
[12 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 5.0049e-07
| PFDsys_PLC | train 1 (PLC only) | 0.0045186 | [8 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 5.4269e-07
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 0.0021961
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.0023813
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 6.9793e-06
|  | Relay collection 2oo3* | 1.0676e-10 | 0.00018733
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0045916

## proximity formula (datasheet)
[7 empty] | T1/2 | 4380
[7 empty] | (T1/3 +8) = | 2928
[7 empty] | T1/2 +8 = | 4388
Beta = 20%
PFDS | PFDsensor (2003) | 0.0024
Sensor+Transmitter |  | 0.0048
two condition |  | 1.536e-05
PFDL_PLC | PFDlogic (PLC) | 6.1321e-06
[6 empty] | component | λ/h | PFD |  | source of data
| PFDlogic Total(1oo2) | 6.1214e-10 |  |  |  | Sensor | 1e-07 | 0.01 | 0.01 | T-book
[6 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
| PFD E- relay set of 2 | 4.0005e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens
| PFD Switch discunnector and contactor | 1.7787e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens
[6 empty] | Switch disconnector | 1e-07 | 0.0002 |  | T-book
PFDFE_PLC | PFD final element PLC train | 1.7787e-09 |  |  |  | Relay | 1e-07 | 2e-05 |  | T-book
[6 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer
PFDFE_relay | PFD final element for Relay train | 4.0023e-06 |  |  |  | E relay | 1.7e-07 | 2e-05 |  | Siemens
[6 empty] | Beta |  | 0.1 | 0.05 | 0.2
| PFD final element total (1oo2) | 9.4917e-15 |  |  |  | contactor Ion | 1e-07 | 6.67e-06 |  | T-book
[6 empty] | Manual safety Stop |  | 0.00219
PFDsys | PFD sys TSS total (Beta= 20%) | 3.1265e-05
PFDsys_PLC | train 1 (PLC only) | 0.0048061
| PFD Relay (2oo3) | 1.6e-09
| Tillqvist communication | 0.012
| Tillqvist (1oo2) | 0.00018647
| Tillqvist sender an reseiver (total) | 7.4867e-05
| Tillqvist collection (2oo3) | 3.7434e-05 |  | Safety Stop function (PLC) | 0.0021961
| Relay 1oo2 | 5.3333e-10 | 4.0005e-06 | Safety Stop function (Relay) | 0.0023845
| Relay collection 2oo3 | 1.0667e-10 |  | Total | 6.9822e-06
PFDL_relay | Total Relay Logic | 7.4869e-05
PFDsys_relay | Total Relay channel | 0.0048789

## TSS-001
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0) | [7 empty] | component | PFD |  | source of data | model
| MRT=8hours | [7 empty] | Sensor and transmitter package | 0.01 | 1e-06 | Datasheet (SIL2) | Yokogawa EJX910A
T1=1 year=8760 hours
Rosemount 3051SMV3M12A3R2E12A1BB4L4Q4
| TSS-TSS-101¾Function for HE cooling mass flow | [7 empty] | Signal conditioner | 0.01 | 1e-06 | Datasheet (SIL2) | Peperl+Fuchs
KFD2-CRG2-1.D
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 1.0298e-06
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 1.0464e-06
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 2.7689e-05 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 0.0045186 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0045916

## TSS-002
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0) | [6 empty] | component | PFD |  | source of data | model
| MRT=8hours | [6 empty] | Switch | 0.01 | 1e-06 | Datasheet (SIL2) | BETA C2-P508H-S2B-B1-N2
| T1=1 year=8760 hours | [10 empty] | Ashcroft B7=61=S<=IP=06=FS=MD=CD2=C4
TSS-TSS-102-Function for HE cooling outlet pressure
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 5.1558e-07
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 5.3221e-07
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 7.051e-06 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 0.0022624 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0023353

## TSS-003
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0) | [6 empty] | component | PFD |  | source of data | model
| MRT=8hours | [6 empty] | Sensor | 0.01 | 1e-06 | Datasheet (SIL2) | Pt-100 sensor by Pentronic
| T1=1 year=8760 hours | [10 empty] | Pt-100 sensor by INOR
[8 empty] | Signal conditioner | 0.01 | 1e-06 | Datasheet (SIL2) | Peperl+Fuchs
| TSS-TSS-103¾Function for HE cooling inlet temperature | [10 empty] | KFD2-GUT-1.D
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 1.0298e-06
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 1.0464e-06
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 2.7689e-05 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 0.0045186 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0045916

## TSS-004
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0) | [7 empty] | component | PFD |  | source of data | model
| MRT=8hours | [7 empty] | Sensor and transmitter package | 0.01 | 1e-06 | Datasheet (SIL2) | Inductive sensor by Emerson PR6423/003-0D1
| T1=1 year=8760 hours | [7 empty] | Signal conditioner | 0.01 | 1e-06 | Datasheet (SIL2)
TSS-TSS-104¾Function for Target wheel rotational speed
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 1.0298e-06
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 1.0464e-06
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 2.7689e-05 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 0.0045186 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0045916

## TSS-005
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0)
| MRT=8hours | [6 empty] | component | PFD |  | source of data | model
| T1=1 year=8760 hours | [6 empty] | Switch | 0.01 | 1e-06 | Datasheet (SIL2) | Barksdale D2T-M18SS
| TSS-TSS-105¾Function for Monolith pressure | [10 empty] | BETA C2-V506H-S2B-B1-N2
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 5.1558e-07
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 5.3221e-07
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 7.051e-06 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 0.0022624 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0023353

## TSS-202
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0) | [5 empty] | component | PFD |  | source of data | model
| MRT=8hours | [5 empty] | Pushbuttons | 2.19e-3 | 10000000 | Manufacturer | XB4BA42
T1=1 year=8760 hours
TSS-TSS-202¾Manual Safety Stop
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 1.3587e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 | Lambda extracted from PLC system total (B=20%) | 1.0298e-06
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book | Lambda extracted from relay system total (B=20%) | 1.0464e-06
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 2.7689e-05 | [8 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[12 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 5.014e-07
| PFDsys_PLC | train 1 (PLC only) | 0.0045186 | [8 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 5.436e-07
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 0.0022001
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.0023853
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 7.0038e-06
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.0045916

## two diversw functions
1oo1 |  |  |  | 1002 |  |  | 2oo3
[8 empty] | (T1/3 +8) = | 2928
[8 empty] | T1/2 +8 = | 4388
4380
Conditions: | DC=0 (λDD=0)
| MRT=8hours | [6 empty] | component | PFD |  | source of data | model
| T1=1 year=8760 hours | [6 empty] | Switch | 0.01 | 1e-06 | Datasheet (SIL2) | Barksdale D2T-M18SS
| Two functions (Worst case) | [10 empty] | BETA C2-V506H-S2B-B1-N2
Beta = 20%
| PFDS | PFDsensor unit (2003) | 0.0022562
| PFD for whole sening part is added two units with minimum SIL2 pfd and considering CCF | PFDsensor unit + system conditioner (2003) | 0.0045125
| two diverse function |  | 2.7175e-05
| PFDL_PLC | PFDlogic (PLC) | 6.1433e-06
[7 empty] | component | λ/h | PFD | B10d | source of data
[7 empty] | Sensor | 2.2789e-06 | 0.01 |  | Tbook
[7 empty] | DI module | 1e-09 | 4.38e-06 |  | Siemens
|  | PFD E- relay set of 2 | 4.0003e-06 |  |  |  | PLC | 1e-09 | 4.38e-06 |  | Siemens |  | in calculation of PFD for relays, CCF is only considered at the end of the chain
|  | PFD Switch discunnector and contactor # | 1.7794e-09 |  |  |  | DO module | 1e-09 | 4.38e-06 |  | Siemens |  | Notice regarding calculation of the items with "# " when CCF is not applicable, beta considered to be zero
[7 empty] | Switch disconnector | 4.5579e-08 | 0.0002 | 25000 | T-book |  | Notice regarding calculation of the items with "*": when PFD calculation of one part is based on calculation of a chain, first the chain was calculated, then, assuming this chain to be one component, its lambda calculated and was used for further calculations
| PFDFE_PLC | PFD final element PLC train | 1.7794e-09 |  |  |  | Relay | 4.5579e-09 | 2e-05 | 250000 | schnider |  | Lambda extracted from PFD for tillquist 1oo2 | 4.269e-08
[7 empty] | Tillqvist | 2.7e-06 | 0.011826 |  | manufacturer (MTBF) |  | Lambda extracted from PFD for relay 1oo2 | 1.2165e-13
| PFDFE_relay | PFD final element for Relay train | 4.0021e-06 |  |  |  | E relay | 4.5579e-09 | 2e-05 | 250000 | schnider
[7 empty] | Beta | 0 | 0.1 | 0.05 | 0.2 |  | Lambda extracted from PLC system total (B=20%) | 7.5933e-09
[7 empty] | contactor Ion | 1.5193e-09 | 6.6667e-06 | 750000 | t-book |  | Lambda extracted from relay system total (B=20%) | 2.4222e-08
[7 empty] | Manual stop | 5e-07 | 0.002194 | 10000000 |  |  | Lambda for sensor subsystem sensor+transmitter | 1.0284e-06
| PFDsys | PFD sys TSS* total (Beta= 20%) | 4.7263e-09 | [9 empty] | Lambda for sensor subsystem switch | 5.1418e-07
[13 empty] | Lambda extracted from PLC system total (B=20%) (safety stop) | 1.4004e-09
| PFDsys_PLC | train 1 (PLC only) | 3.332e-05 | [9 empty] | Lambda extracted from relay system total (B=20%) (safety stop) | 4.3602e-08
|  | PFD Relay (2oo3)# | 1.6015e-09
|  | Tillqvist communication | 0.012
|  | Tillqvist (1oo2)# | 0.00018732
|  | Tillqvist sender an reseiver (total) | 7.511e-05 |  | Safety Stop function (PLC) | 6.145e-06
|  | Tillqvist collection (2oo3)* | 3.7555e-05 |  | Safety Stop function (Relay) | 0.00019133
|  | Relay 1oo2# | 5.3382e-10 |  | Total | 1.569e-09
|  | Relay collection 2oo3* | 1.0676e-10
| PFDL_relay | Total Relay Logic | 7.5111e-05
| PFDsys_relay | Total Relay channel | 0.00010629