## IOC - TSS Gateway PLC
Simplified IO list (seen from the IOC's perspective) TSS Gateway PLC Tag: Tag name in the TSS Gateway PLC program. PV Name: EPICS Process Variable name Description: Describing the purpose of the Device Tag. R/W: Describes whether the system in focus is reading, writing, or reading and writing to the Device Tag. Protocol: Data transfer protocol, e.g. profinet, modbus... Data Type: e.g. Bool, Real, Int... Unit: Unit of the value from the Device Tag. Archiver Scan rate: The rate at which the Device Tag archived. "Monitor" implies "update on change". OPI: 1 if this variable should be presented in the OPI, 0 if not.
ESS Name 1 | ESS Name 2 | Property | PV Name1 section-subsection:discipline-device-index | PV Name2 section-subsection:discipline-device-index | Description | R/W | Protocol | Data Type | Unit | Archiver Scan Rate (s) | OPI
TSS-Mon:Ops-TS-101 | TS-SPS:F07-TS-101 | HeInletTempSwitch | TSS-Mon:Ops-TS-101:HeInletTempSwitch | TS-SPS:F07-TS-101:HeInletTempSwitch | He cooling inlet temperature switch A | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-TS-102 | TS-SPS:F07-TS-102 | HeInletTempSwitch | TSS-Mon:Ops-TS-102:HeInletTempSwitch | TS-SPS:F07-TS-102:HeInletTempSwitch | He cooling inlet temperature switch B | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-TS-103 | TS-SPS:F07-TS-103 | HeInletTempSwitch | TSS-Mon:Ops-TS-103:HeInletTempSwitch | TS-SPS:F07-TS-103:HeInletTempSwitch | He cooling inlet temperature switch C | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-TS-100 | TS-SPS:F07-TS-100 | HeInletTempVoteStatus | TSS-Mon:Ops-TS-100:HeInletTempVoteStatus | TS-SPS:F07-TS-100:HeInletTempVoteStatus | He cooling inlet temperature safety logic solver vote block | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-PS-101 | TS-SPS:F07-PS-101 | HeOutletPresSwitch | TSS-Mon:Ops-PS-101:HeOutletPresSwitch | TS-SPS:F07-PS-101:HeOutletPresSwitch | He cooling outlet pressure switch A | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-102 | TS-SPS:F07-PS-102 | HeOutletPresSwitch | TSS-Mon:Ops-PS-102:HeOutletPresSwitch | TS-SPS:F07-PS-102:HeOutletPresSwitch | He cooling outlet pressure switch B | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-103 | TS-SPS:F07-PS-103 | HeOutletPresSwitch | TSS-Mon:Ops-PS-103:HeOutletPresSwitch | TS-SPS:F07-PS-103:HeOutletPresSwitch | He cooling outlet pressure switch C | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-100 | TS-SPS:F07-PS-100 | HeOutletpresVoteStatus | TSS-Mon:Ops-PS-100:HeOutletpresVoteStatus | TS-SPS:F07-PS-100:HeOutletpresVoteStatus | He cooling outlet pressure safety logic solver vote block | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-PS-201 | TS-SPS:F07-PS-201 | MonolithPresSwitch | TSS-Mon:Ops-PS-201:MonolithPresSwitch | TS-SPS:F07-PS-201:MonolithPresSwitch | Monolith pressure switch A | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-202 | TS-SPS:F07-PS-202 | MonolithPresSwitch | TSS-Mon:Ops-PS-202:MonolithPresSwitch | TS-SPS:F07-PS-202:MonolithPresSwitch | Monolith pressure switch B | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-203 | TS-SPS:F07-PS-203 | MonolithPresSwitch | TSS-Mon:Ops-PS-203:MonolithPresSwitch | TS-SPS:F07-PS-203:MonolithPresSwitch | Monolith pressure switch C | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-PS-200 | TS-SPS:F07-PS-200 | MonolithPresVoteStatus | TSS-Mon:Ops-PS-200:MonolithPresVoteStatus | TS-SPS:F07-PS-200:MonolithPresVoteStatus | Monolith pressure safety logic solver vote block | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-SS-101 | TS-SPS:F07-SS-101 | HeOutletVelSwitch | TSS-Mon:Ops-SS-101:HeOutletVelSwitch | TS-SPS:F07-SS-101:HeOutletVelSwitch | He cooling outlet velocity switch A | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-102 | TS-SPS:F07-SS-102 | HeOutletVelSwitch | TSS-Mon:Ops-SS-102:HeOutletVelSwitch | TS-SPS:F07-SS-102:HeOutletVelSwitch | He cooling outlet velocity switch B | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-103 | TS-SPS:F07-SS-103 | HeOutletVelSwitch | TSS-Mon:Ops-SS-103:HeOutletVelSwitch | TS-SPS:F07-SS-103:HeOutletVelSwitch | He cooling outlet velocity switch C | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-100 | TS-SPS:F07-SS-100 | HeOutletVelVoteStatus | TSS-Mon:Ops-SS-100:HeOutletVelVoteStatus | TS-SPS:F07-SS-100:HeOutletVelVoteStatus | He cooling outlet velocity safety logic solver vote block | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-SS-201 | TS-SPS:F07-SS-201 | WheelRotVelSwitch | TSS-Mon:Ops-SS-201:WheelRotVelSwitch | TS-SPS:F07-SS-201:WheelRotVelSwitch | Wheel rotation velocity switch A | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-202 | TS-SPS:F07-SS-202 | WheelRotVelSwitch | TSS-Mon:Ops-SS-202:WheelRotVelSwitch | TS-SPS:F07-SS-202:WheelRotVelSwitch | Wheel rotation velocity switch B | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-203 | TS-SPS:F07-SS-203 | WheelRotVelSwitch | TSS-Mon:Ops-SS-203:WheelRotVelSwitch | TS-SPS:F07-SS-203:WheelRotVelSwitch | Wheel rotation velocity switch C | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-SS-200 | TS-SPS:F07-SS-200 | WheelRotVelVoteStatus | TSS-Mon:Ops-SS-200:WheelRotVelVoteStatus | TS-SPS:F07-SS-200:WheelRotVelVoteStatus | Wheel rotation velocity safety logic solver vote block | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-Sw-101 | TS-SPS:F07-Sw-101 | InitShutdownHeTemp | TSS-Mon:Ops-Sw-101:InitShutdownHeTemp | TS-SPS:F07-Sw-101:InitShutdownHeTemp | Safety Instrumented Function 001 initiated, shutdown due to He cooling system temperature | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-102 | TS-SPS:F07-Sw-102 | InitShutdownHePres | TSS-Mon:Ops-Sw-102:InitShutdownHePres | TS-SPS:F07-Sw-102:InitShutdownHePres | Safety Instrumented Function 002 initiated, shutdown due to He cooling system pressure | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-103 | TS-SPS:F07-Sw-103 | InitShutdownHeVel | TSS-Mon:Ops-Sw-103:InitShutdownHeVel | TS-SPS:F07-Sw-103:InitShutdownHeVel | Safety Instrumented Function 003 initiated, shutdown due to He cooling system outlet velocity | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-104 | TS-SPS:F07-Sw-104 | InitShutdownWheelVel | TSS-Mon:Ops-Sw-104:InitShutdownWheelVel | TS-SPS:F07-Sw-104:InitShutdownWheelVel | Safety Instrumented Function 004 initiated, shutdown due to wheel rotation velocity | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-105 | TS-SPS:F07-Sw-105 | InitShutdownMonoPres | TSS-Mon:Ops-Sw-105:InitShutdownMonoPres | TS-SPS:F07-Sw-105:InitShutdownMonoPres | Safety Instrumented Function 005 initiated, shutdown due to monolith pressure | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-201 | TS-SPS:F07-Sw-201 | CompletedShutdownHeTemp | TSS-Mon:Ops-Sw-201:CompletedShutdownHeTemp | TS-SPS:F07-Sw-201:CompletedShutdownHeTemp | Safety Instrumented Function 001 completed, shutdown due to He cooling system temperature | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-202 | TS-SPS:F07-Sw-202 | CompletedShutdownHePres | TSS-Mon:Ops-Sw-202:CompletedShutdownHePres | TS-SPS:F07-Sw-202:CompletedShutdownHePres | Safety Instrumented Function 002 completed, shutdown due to He cooling system pressure | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-203 | TS-SPS:F07-Sw-203 | CompletedShutdownHeVel | TSS-Mon:Ops-Sw-203:CompletedShutdownHeVel | TS-SPS:F07-Sw-203:CompletedShutdownHeVel | Safety Instrumented Function 003 completed, shutdown due to He cooling system outlet velocity | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-204 | TS-SPS:F07-Sw-204 | CompletedShutdownWheelVel | TSS-Mon:Ops-Sw-204:CompletedShutdownWheelVel | TS-SPS:F07-Sw-204:CompletedShutdownWheelVel | Safety Instrumented Function 004 completed, shutdown due to wheel rotation velocity | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Sw-205 | TS-SPS:F07-Sw-205 | CompletedShutdownMonoPres | TSS-Mon:Ops-Sw-205:CompletedShutdownMonoPres | TS-SPS:F07-Sw-205:CompletedShutdownMonoPres | Safety Instrumented Function 005 completed, shutdown due to monolith pressure | R | TCP Socket | Bool | N/A | 1
TSS-Mon:Ops-Txt-101 | TS-SPS:F07-Txt-101 | TSSBeamPerm | TSS-Mon:Ops-Txt-101:TSSBeamPerm | TS-SPS:F07-Txt-101:TSSBeamPerm | TSS beam permission string | R | TCP Socket | Char | N/A | 1 | 1
TSS-Mon:Ops-Txt-102 | TS-SPS:F07-Txt-102 | TSSBeamAim | TSS-Mon:Ops-Txt-102:TSSBeamAim | TS-SPS:F07-Txt-102:TSSBeamAim | TSS beam aim string | R | TCP Socket | Char | N/A | 1 | 1
TSS-Mon:Ops-Com-101 | TS-SPS:F07-Com-101 | ModbusComConnected | TSS-Mon:Ops-Com-101:ModbusComConnected | TS-SPS:F07-Com-101:ModbusComConnected | TSS Gateway PLC / IOC Modbus communication connected | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-Com-102 | TS-SPS:F07-Com-102 | S7ComConnected | TSS-Mon:Ops-Com-102:S7ComConnected | TS-SPS:F07-Com-102:S7ComConnected | TSS Gateway PLC / IOC s7plc communication connected | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-Com-103 | TS-SPS:F07-Com-103 | PLCHashOk | TSS-Mon:Ops-Com-103:PLCHashOk | TS-SPS:F07-Com-103:PLCHashOk | TSS Gateway PLC hash correct | R | TCP Socket | Bool | N/A | 1 | 1
TSS-Mon:Ops-Com-104 | TS-SPS:F07-Com-104 | EPICSComAlive | TSS-Mon:Ops-Com-104:EPICSComAlive | TS-SPS:F07-Com-104:EPICSComAlive | EPICS Communication all working? | R | TCP Socket | Bool | N/A | 1 | 1
From John
TGT-WHL:TSS-TS-idx:HeInletTempOk.VAL
TGT-WHL:TSS-TS-idx:T-RB.VAL | [5 empty] | SLS - Safety Logic Solver. SLS-100 means SLS number one. TS-102 means Temperature Switch number two used for SLS number one
We need to check the SLS name, it clashes between different switch types with the above nomenclature