## Slide 1: Recapture of CDR1 - TSS requirements - TSS CDR2
Mikael Olsson
Control Engineer
www.europeanspallationsource.se
8 April, 2019

## Slide 2: TSS documentation map - CDR 2
Software test specification
Concept
ESS-0037596
Hazard analysis overview
ESS-0050077
System requirements
ESS-0002776
Safety PLC function specification
ESS-0043617
ICD-R:s
ESS-0016380
ESS-0022915
ESS-0030063
ESS-0030068
ESS-0042356
ESS-0048755 ESS-0032009
ESS-0198545
ESS-0288103
Life-cycle process
Gateway PLC function specification
ESS-0464719
TSS trip limits ESS-0287373
V&V plan
ESS-0048372
Architecture ESS-0045067
Hazard analysis process
ESS-0041755
Target Station
RSFs & DiD ESS-0050185
Accidents reports ESS-0040075
ESS-0044348
ESS-0050081
ESS classification
ESS-0016468
Categorization Monolith Events
ESS-0454232
Categorization Monolith Events
ESS-0454232
ESS rules for I&C classification & design
ESS-0054158
TSS classification
ESS-0218018
System design ESS-0321310
Electrical design (ePLAN)
Prob. analysis
ESS-0052608
FAT specification
FIT specification
SAT specification
SIT specification
Concept of operation ESS-0485264
Software test report
FAT report
FIT report
SAT report
SIT report
KFM
P&ID
FMEA
ESS-0047128
Classification list ESS-0191808
Qualification report
Instrumentation technical specification
Normal environmental conditions
ESS-0085658
Installation plan

## Slide 3: From CDR1 - TSS functions
Radiation safety functions, identified in AAs | Class | Functions, not identified in AAs | Class
RSF-68: Target wheel rotational speed too slow | EICPA | Static permit beam (bypass) | EICPA
RSF-69: He pressure too low | EICPA | Manual operational (start/stop) | EIC0
RSF-70: Monolith vessel pressure too high | EICPA | Manual safety stop | EICPB
RSF-71: He inlet temperature too high | EICPA | Operational monitoring | EIC0
RSF-72: He mass flow too low | EICPA | Safety monitoring | EIC0

## Slide 4: From CDR1 - TSS radiation safety functions
# | Function | Trip level | Trip time [s]
 | Prevent beam from hitting Target if… |  | 
1 | Target wheel rotational speed is … | < 9 rpm | 3
2 | He pressure is … | < 8 bar(a) | 25
3 | Monolith vessel pressure is … | > 0.5 bar(a) | 2.5
4 | He inlet temperature is … | > 70 C | 25
5 | He mass flow is … | < 1.75 kg/s | 25
# | Function | Trip level | Trip time [s]
 | Prevent beam from hitting Target if… |  | 
1 | Target wheel rotational speed is … | < 9 rpm | 3
2 | He pressure is … | < 8 bar(a) | 25
3 | Monolith vessel pressure is … | > 0.5 bar(a) | 2.5
4 | He inlet temperature is … |  | 25
5 | He mass flow is … | < 1.75 kg/s | 25

## Slide 5: From CDR1 - TSS functions not identified in AAs
Static permit beam (bypass of Radiation safety functions)
  static permit for beam production independent of the target mode, requires that beam is direct to dump
  Accelerator Division requires beam production for maintenance purposes even when the target is not ready for beam
Manual operational start/stop
  Start = intentional permit of beam production
  Stop = set in safe state, for maintenance of TSS, periodic testing of TSS, planned downtime, etc
  It is assumed that this function is used as part of a sequence of actions defined for operation of the facility
  SSM condition C25 and 29
Manual safety stop
  Emergency stop, in case of antagonistic event, loss of information in main control room, etc.
  SSM deems that the operators shall be able to manually shut down with a safety system
Operational monitoring
  provide TSS status and status history to the operator in the main control room
  SSM condition C3 and C29
Safety monitoring
  Provide critical TSS status to the operator in the main control room, during defense in depth L3
  Monitored data may be a subset of “Operational monitoring”
  May be used to initiate manual actions in the future (not yet credited)
  SSM condition C3 and C29

## Slide 6: From CDR1 - subset of constraint requirements
Redundancy, diversity, physical separation, functional separation
Passive solutions, fail-safe concept
Deterministic assessment of reliability
Probabilistic assessment of reliability (PFD 10-4)
IEC 61226, 61513: system design
IEC 61511: probabilistic assessment

## Slide 7: From CDR1 - Conceptual TSS architecture, basic interfaces
ESS-0037596, TSS concept
Critical process values are monitored and evaluated continuously, from the target station systems
Actuation at the Ion source and the RFQ in the Accelerator
Control and monitoring of beam direction to bypass TSS RSFs
Information of TSS status to operator in the Main control room
  Benefit ICS infrastructure
Fail-safe concept
  Loss of power or communication will lead to actuation
Securing beam to dump
, Main control room