## Slide 1: TSS System Architecture ESS-0045067 - TSS CDR2
Mikael Olsson
Control Engineer
www.europeanspallationsource.se
8 April, 2019

## Slide 2: TSS System Architecture - agenda
Scope and purpose
Architecture
Layout and physical separation
Summary

## Slide 3
Scope and purpose

## Slide 4: TSS architecture - scope and purpose
Scope:
IEC 61513, 3.27: To define organisational structure of the system
  main functions, class, subsystems, interconnections between subsystems, independence between subsystems, priority, voting, HMI
Purpose:
The purpose is to contribute to further detailed design, such as instrumentation, choice of components, electrical design, application software design, etc.

## Slide 5
Architecture

## Slide 6: TSS architecture - overall architecture
Safety logic - hardware based
Safety logic – software based
Operation & monitoring - software based
Safety sensors
Safety actuators
Other systems
Start
Radiation safety system - class EICPA or EICPB
Operational system - class EIC0

## Slide 7: TSS architecture - radiation safety function
– hardware based train
– software based train
Sensors
Communication and 2oo3 voting
Actuation (trip)
A1 (ion)
A3 (RFQ)
A2 (ion)
A4 (RFQ)
One radiation safety function
Diverse equipment
A
B
C

## Slide 8: TSS architecture - radiation safety function
IEC 61513 ‘NPP general requirements’, Annex C, Example 5
“typical situations” which has “low potential causes of CCF”.
“diverse protection functions”
“two different systems”
“Different (diverse) actuation systems”
IEC 62340 ‘NPP coping with CCF’, 5.2
“For I&C systems that perform category A functions the appropriate application of redundancy combined with voting mechanisms has been proven to meet the single failure criterion. This design ensures that the likelihood of a failure of such I&C systems is very low.”
2oo3 voting, two trains
Sharing sensors
IEEE 384 ‘Independence of Class 1E’,
7.2.1: “Electrical isolation methods shall be used as required in instrumentation and control circuits to maintain the independence of redundant circuits”
7.2.2: “acceptable isolation devices … relays, fiber optic, circuit breakers…”
IEC 62340 ‘NPP coping with CCF’,
7.1: “I&C systems perform their safety functions independently if a postulated failure of one of these I&C systems does not prevent the other systems from performing their functions as intended”

## Slide 9: TSS architecture - radiation safety function
– hardware based train
– software based train
Sensors
Communication and 2oo3 voting
Actuation (trip)
A1 (ion)
A3 (RFQ)
A2 (ion)
A4 (RFQ)
Several radiation safety functions
Diverse equipment
A
B
C
Target wheel rotation
He pressure
Monolith pressure
He temperature
He mass flow
5
5
5

## Slide 10: TSS architecture - manual stop
– hardware based train
– software based train
Manual stop control
Monitoring and communication
Actuation (trip)
A1 (ion)
A3 (RFQ)
A2 (ion)
A4 (RFQ)
Manual stop
Note, both ‘manual safety stop’ and ‘manual operational stop’ are designed this way
Diverse equipment

## Slide 11: TSS architecture - manual stop
IEC 61513 ‘NPP general requirements’, Annex C, Example 3
“typical situations” which has “low potential causes of CCF”.
Manual control:
  “manual control acting downstream of voter” as defence against “A failure in the two out of three voting”
  “same protection action”

## Slide 12: TSS architecture - bypass function
Bypassing five radiation safety functions that monitor target system parameters, and replacing them with a new radiation safety function that prevents the beam from going to the target.
- Disconnect dipole magnet electrical supply
- Disconnect dipole magnet electrical supply
- Switch at ion source
Monolith pressure
Helium temperature
Helium pressure
Helium massflow
Wheel speed
All conditions fulfilled?
If YES: override with beam permit
Redundant means to direct beam to dump
Diverse setting (confirmation)
- Switch at RFQ
Position feedback
A
A
A
A
A
B
B
B
B
B
C
C
C
C
C
2oo3
1
2
3
4
1
2
3
4

## Slide 13: TSS architecture - bypass
No real support in standards how to organise/arrange bypass elements
IEC 61226, 7.3.2.1
“Testing may require suppression of output signals, or the provision of bypass facilities”.
IEC 61511, 11.7.1.2
“… minimize … the need to bypass the system while the unit is running”.
“… facilities for protection against operator error”.
Diverse equipment
– hardware based train
– software based train
Bypass control
Monitoring, 4oo4 evaluation and communication
Actuation (bypass)
A1 (ion)
A3 (RFQ)
A2 (ion)
A4 (RFQ)
Bypass

## Slide 14: TSS architecture
Safety PLC train
Monolith pressure
Dipole magnet
Relay train
2oo3
Ion source
Beam dump
TSS
RFQ
Basic process control system
Proton beam
Target wheel
A
B
C
Helium temperature
Helium pressure
Helium mass flow
Machine protection
RFQ power
Ion source power
Actuator 4
Actuator 2
Actuator 1
Actuator 3
Wheel speed
Manual operational stop
Relay PLC
Relay PLC
Relay PLC
5
5
5
2oo3
Manual safety stop
Bypass
Manual operational stop
Manual safety stop
Bypass
Manual safety stop
Manual operational stop
Channel

## Slide 15: TSS architecture - operational system
Monitors status of components in the radiation safety system
GUI, alarm handling, manual start, communication to other systems
Software based (PLC system with distributed I/O:s)
Separate cables and control components
Does not include redundancy or diversity
Electrically isolated from the radiation safety system
No impact on the radiation safety system
  Cannot prevent radiation safety functions
  Cannot prevent manual stop
  Cannot affect bypass
  Cannot generate a spurious trip
Note, ‘manual operational stop’ is performed by the radiation safety system, due to availability

## Slide 16: TSS architecture - basic state machine
Beam production prevented by TSS
Beam production allowed by TSS
Bypass
No Bypass
Any bypass condition not fulfilled
All bypass conditions fulfilled
Manual operational stop
Manual start
2oo3 channels trip
No beam
Beam allowed
Manual safety stop

## Slide 17
Layout and physical separation

## Slide 18: TSS layout - Target utility area
TSS room #1
Ion source and RFQ
PLC 2oo3
Relay 2oo3
Actuators

## Slide 19: TSS layout - Target utility area – separation
TSS separation
Copper cables
Redundant cables in separate metallic pipes
Redundant control cabinets on separate levels (fire zones)
Functions/sensors in separate areas (fire zones)
IEC 60709, IEEE 384: “Hazard area”
IEC 60709:
  “for plant failure and external failure events … greater physical separation [than 30 cm horizontal, 80 cm vertical] including barriers and/or safety structures shall be applied.”
  “For lesser separation distances [than 30 cm horizontal, 80 cm vertical] in hazardous areas, the degree of hazards (such as size of the fire or pipe break) and mitigating measures (such as sprinklers) should be considered”.
IEEE 384:
  “Hazard area”: “Protection … shall be accomplished by the use of barriers, restraints, separation distance, or appropriate combination thereof.”

## Slide 20: TSS layout - ESS facility
TSS #1 - PLC 2oo3
Target utility block
Klystron gallery (G02)
Dipole magnet
RFQ - Relay 2oo3
Ion source - Relay 2oo3
MCR - manual stop
Front end building
Target buidling
Relay system cables
Safety PLC system cables

## Slide 21: TSS layout - outside Target utility area - separation
TSS separation
Fiber cables
Redundant cables in separate metallic pipes
>0.1 m between metallic pipes
Routed in same area (fire zone)
IEC 60709, IEEE 384: “Nonhazard area”
IEC 60709:
  “redundant groups … separate cable routes”
  If less separation than 30 cm (horizontal) and 80 cm (vertical), then “enclosed raceways that qualify as barriers” shall be used
IEEE 384:

## Slide 22: TSS layout - separation - conclusions
Target utility area is considered as a “Hazard area”
  Possible events that cause accidents, or are consequences of accidents, that demand TSS to work
  Strong physical separation
Areas outside Target utility area are considered as “Nonhazard areas”
  No event that causes accidents, or is consequence of accidents, that demand TSS to work
  Less physical separation
According to standards

## Slide 23
Summary

## Slide 24: TSS architecture - RFPD consideration
Redundancy
  2oo3 of sensors, two communication and voting systems (trains), four actuators, two actuation locations (ion source and RFQ)
Diversity
  Different functions (THe, PHe, PM, ṁ, ω), different types of communication, different voting systems (hardware and software based), different types of actuators
Functional separation
  Electrical isolation between radiation safety system and operational system
  Electrical isolation between the trains
  Electrical isolation between the channels
Physical separation
  Channels in separate cable paths, even at separate levels inside Target utility area
The level of RFPD to withstand independent failures and external events is assessed by the TSS FMEA.
We feel confident when entering the assessment phase…

## Slide 25: TSS system architecture
Thank you!