## Slide 1: TSS Design
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 2: TSS basic design rules
TSS system design is governed by SSM conditions
  Diversity
  Redundancy
  Separation
    Functional
    Physical
  Fail safe
  Manual safety stop button
System design based on IEC61226 & IEC 61513

## Slide 3: TSS – Main Interfaces
Input- Conditions
  Mass Flow in Target Primary Cooling System
  Pressure in Target Primary Cooling System
  Temperature in Target Primary Cooling System
  Rotation speed in Target Wheel system
  Pressure in Monolith Vessel
  Manual Safety Stop Button in Main Control Room
Output- Actions
  2 Actuators for cutting the power supply to the Ion Source
  2 Actuators for cutting the power supply to the RFQ

## Slide 4: Simplified block diagram TSS

## Slide 5: TSS Main Components
Field Instrumentation
Primary logic in A, B & C-channel,
Separated networks for Safety trains (Relay/PLC)
Relay-train including a HW-based 2oo3 voting
Safety PLC-train including a SW-based 2oo3 voting
Actuator type A & B
Dipole Magnet
Gateway PLC- Non Safety functions

## Slide 6: TSS – Non Safety Interfaces
TSS Operator Panel in MCR
  Part of TSS, owned by TSS
  Must be designed together with ESS Operations Group
Gateway PLC
  The TSS tool for interfacing with non-safety tasks & other systems
  Ongoing definition of the interface with EPICS for OPI, Archiving, Operator Notification via the Gateway PLC – currently PDR-ready for ICS-owned TSS Monitoring System (TSSMS)
  The technical base (protocol) is designed together with ICS
Operator work station in MCR (EPICS)
  Full scope of User Interface is not decided yet
  Read only interface, alarm displaying, no alarm handling
  Must be designed together with ESS Operations Group

## Slide 7: TSS components - location

## Slide 8: TSS General design
Any questions?

## Slide 9: TSS Field Instrumentation
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 10: General requirements on field instruments - conditions
Qualified for use in the environment that can occur
Components Of The Shelf - COTS
Proven design
Well known suppliers
Aiming for simplicity
The same sensing equipment provides both the trains with the process status

## Slide 11: Overview TSS equipment
TSS room #1
Ion source and RFQ
PLC 2oo3
Relay 2oo3
Actuators

## Slide 12: Mass Flow in Helium cooling circuit I

## Slide 13: Mass Flow in Helium cooling circuit II
The process connections are in D02.115.4003, Venturi principle is used
Shared venturi between the 3 transmitters
Impulse piping used to transfer the pressure to a non radiation area
The transmitter provides a calculated mass flow value based on
  static pressure measured from – leg
  dP measured from + & - leg
  temperature measured by independent Pt-100 element attached to process in D02.115.3067
  The mass weight of Helium 4 gas
The 3 transmitters will be located in D02.115.3064, D02.103.3064 & D02.085.3064
Each transmitter connects to a signal conditioner that interfaces towards Relay-train & PLC-train electrical independent of each other

## Slide 14: Pressure in Helium cooling circuit
The process connections are in D02.115.3064
The pressure switch provides open/closed switches towards the Relay-train & PLC-train electrical independent of each other
The 3 pressure switches will be located in D02.115.3064, D02.103.3064 & D02.085.3064
Impulse piping used to transfer the pressure to a non radiation area
This pressure switch will not be the same type and brand as the one measuring monolith vessel pressure due to CCF

## Slide 15: Temperature in Helium cooling circuit
The process connections are in D02.115.3064
4-wire technique is used to get high resolution
The 3 temperature transmitters will be located in D02.115.3064, D02.103.3064 & D02.085.3064
Each transmitter connects to a signal conditioner that interfaces towards Relay-train & PLC-train electrical independent of each other

## Slide 16: Rotation speed in Target Wheel system
The process connection is in D02.115.4001
Inductive sensor connected to electrical units in D02.115.4005
The 3 main electronic units will be located in D02.115.3064, D02.103.3064 & D02.085.3064
Each main electronic unit connects to a signal conditioner that interfaces towards the Relay-train & PLC-train electrical independent of each other

## Slide 17: Pressure in Monolith Vessel
The process connections are in D02.115.4001
The pressure switch provides open/closed switches towards the Relay-train & PLC-train electrical independent of each other
The 3 pressure switches will be located in D02.115.3064, D02.103.3064 & D02.085.3064
Impulse piping (Dimension DN25) used to transfer the pressure to a non radiation area
This pressure switch will not be the same type and brand as the one measuring monolith vessel pressure due to CCF

## Slide 18: TSS Field Instrumentation
Any questions?

## Slide 19: TSS Channels
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 20: TSS Channels
The channels collect the input sub-conditions
  i.e. Helium Mass flow is a condition
  Channel A (B,C) Helium mass flows are sub-conditions
  Channel A (B,C) collects the 5 sub-conditions
Built in series like a chain, logic OR-gate
The design is picked up from Nuclear Industry
Channels in Relay-train & PLC-train shall have the same basic behavior
The Logic for Relay-train is based on HW
The logic for PLC-train is based on SW

## Slide 21
TSS room #1
Ion source and RFQ
PLC 2oo3
Relay 2oo3
Actuators

## Slide 22: TSS Channels
Any questions?

## Slide 23: TSS Network
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 24: TSS networks
3 Separated networks for Relay-train, PLC-train & Gateway
Example:
Safety CPU <-> To its own Cabinet
Safety CPU <-> Channel A Cabinet
Safety CPU <-> Channel B Cabinet
Safety CPU <-> Channel C Cabinet
Safety CPU <-> Main Control Room Cabinet (MCR)
Safety CPU <-> Dipole Magnet Cabinet (DM)
Safety CPU <-> RFQ Control Cabinet
Safety CPU <-> ION Source Control Cabinet.
2 of the networks, Relay-train and PLC-train uses different type and brand of components

## Slide 25: TSS overview

## Slide 26: TSS Network
Any questions?

## Slide 27: TSS Voting
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 28: TSS Channels to voting
Channel information communicated for voting
Fiber optics are used to transfer signals long distance
The relays perform the voting logic for the Relay train
This is done by SW in the PLC-train

## Slide 29: TSS logic
2oo3 Created close to the actuators in Relay-train
Created by SW in PLC-train
Connects to 2+2 actuators that performs the power break up of feeding the Ion-source and the RFQ

## Slide 30: TSS logic II
Stop relay logic includes the manual safety stop button

## Slide 31: TSS Voting
Any questions?

## Slide 32: TSS Actuators
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 33: TSS Actuators
Ion-source, both contactors shown

## Slide 34: TSS Actuators
RFQ, both Switch disconnectors shown

## Slide 35: TSS Actuators
Any Questions

## Slide 36: TSS Dipole Magnet
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 37: TSS Logic for Dipole magnet DM I

## Slide 38: TSS Dipole magnet DM II
When activated it overrides the 2oo3-voting
Activation is done in 3 independent steps
  Turn off the two local switches at power supply to DM
  Turn on (confirmation) the two local switches at RFQ & Ion-source cabinets
  Start by turn local dial in MCR to activate
Doing it the wrong way will not override the 2oo3
When reversing the same order but dial for start TSS

## Slide 39: TSS Dipole Magnets
Any questions?

## Slide 40: TSS Gateway
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 41: Gateway PLC – typical use
Feedback of signals from the actuators

## Slide 42: Gateway PLC- GW
Gateway PLC is the TSS operational system
Handles non safety signals
  Internal supervision in cabinets
  Controlled signals
  Interface between TSS & EPICS (MCR)
  Have its own network connecting the TSS cabinets
If GW breaks down, no impact on TSS safety function

## Slide 43: Gateway PLC - Functional separation
What is functional separation (Independence)?
  SSMFS, Guiding document C18:
The purpose of functional separation is to achieve a design where SSC (Structure, System or Components) which are part of safety groups are sufficiently separated, for example through isolation devices, switches, valves, diodes, etc., so that the risk of common cause failures is minimised
  IEC61513:
    The ability to perform a required function is unaffected by the other equipment
    Means to achieve independence in the design are electrical isolation
How can functional separation be solved?
  Galvanically separated from Relay-train & PLC-train
    Uses relay components to separate
    Uses an independent network
    Used for feedback of signals
    Used for controlled actions in the TSS

## Slide 44: TSS Gateway
Any questions?

## Slide 45: TSS Test facilities
Ola Ingemansson
Electrical & Instrumentation Engineer
www.europeanspallationsource.se
5 April, 2019

## Slide 46: TSS Test-bench
In the workshop we have a condensed version of the TSS
We can
  Run process simulations using real field instruments
  Run test sequences
  Run test HMI together with Operations group
We will
  Be able to verify the chosen logic
  Be able to produce operational instructions
  Be able to produce maintenance instructions

## Slide 47: TSS Design
That completes the TSS design presentation
Any Questions?