## Slide 1
TRIP
MEM
A
B
C
3oo3 (Start)
DM
OR
Safe Stop
AND
Maintenance
OFF
By-pass
AND
AND
Channels tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop tripped (button being pushed by OP)
Maintenance/operation key off

## Slide 2
TRIP
MEM
A
B
C
3oo3 (start)
DM
OR
Safe Stop
AND
Maintenance
OFF
By-pass
AND
AND
Channels tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop ok (button released)
Maintenance/operation key off

## Slide 3
TRIP
MEM
A
B
C
3oo3
(start)
DM
OR
Safe Stop
AND
Maintenance
OFF
By-pass
AND
AND
Channels sensors ok but waiting for “Channel Reset”
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key off
R
R
R

## Slide 4
R
A
TRIP
MEM
3oo3 (start)
DM
OR
Safe Stop
AND
Maintenance
OFF
By-pass
AND
AND
Channels ok “Channel Reset” executed by OP
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key off
..Trip Memory ready for reset “Waiting actuator Reset”
R
R
B
C

## Slide 5
R
A
2oo3
DM
OR
Safe Stop
AND
Maintenance
OFF
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key off
Trip Memory is reset by OP (not tripped anymore)
Channels voting becomes active (3oo3 ->2oo3)
R
R
B
C
TRIP
MEM

## Slide 6
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
OFF
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key turned on to “Operation mode” by OP
.. so actuator now waits for Start command
R
R
B
C
TRIP
MEM
S
A

## Slide 7
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
OP pushed “Start button” in MCR
R
R
B
C
TRIP
MEM
S
A
ON

## Slide 8
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
A channel tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
B
C
TRIP
MEM
S
A
ON

## Slide 9
A
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
A channel trip corrected (by engineer or process value back in threshold)
.. channel waiting for reset
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
B
C
TRIP
MEM
S
ON

## Slide 10
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
A channel is reset by OP
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
B
C
TRIP
MEM
S
ON
A

## Slide 11
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
B channel tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
B
C
TRIP
MEM
S
ON
A

## Slide 12
R
3oo3 (start)
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
B and C channels tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
…Trip memory is cleared and actuator goes off
R
R
B
C
TRIP
MEM
S
OFF
A

## Slide 13
R
3oo3 (start)
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels tripped
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
B
C
TRIP
MEM
S
OFF
A

## Slide 14
B
C
A
R
3oo3 (start)
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ready again - waiting for reset
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
R
R
TRIP
MEM
S
OFF

## Slide 15
TRIP
MEM
R
3oo3 (start)
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok ”Channel Reset” is executed by OP
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
..Trip Memory ready for reset “Waiting actuator Reset”
R
R
S
OFF
B
C
A

## Slide 16
OFF
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
Trip Memory is reset by OP (not tripped anymore)
..channels voting becomes active (3oo3 ->2oo3)
…actuator waits for “Start command”
R
R
S
B
C
A
TRIP
MEM

## Slide 17
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation key on
Start command given by OP
R
R
S
ON
B
C
A
TRIP
MEM

## Slide 18
R
2oo3
DM
OR
Safe Stop
AND
Maintenance
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation turned off
R
R
S
OFF
B
C
A
TRIP
MEM

## Slide 19
OFF
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation turned back On
.. Waiting for “Start”
R
R
S
B
C
A
TRIP
MEM

## Slide 20
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation switch on
Start command given by OP
R
R
S
B
C
A
TRIP
MEM
ON

## Slide 21
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switch 1(or 2) turned off
DM confirmation switch off
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
A
TRIP
MEM
ON

## Slide 22
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switch 1 off
DM switch 2 turned off
DM confirmation switch off
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
A
TRIP
MEM
ON

## Slide 23
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switch 1 off
DM switch 2 off
DM confirmation switch turned on (locally on ION/RFQ)
.. Waiting DM condition Reset (from MCR)
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
ON
R
A

## Slide 24
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switch 1 off
DM switch 2 off
DM confirmation on
DM Reset by OP
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
ON
A

## Slide 25
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channel A Trip
DM switch 1 off
DM switch 2 off
DM confirmation on
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
ON
A

## Slide 26
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channel A+B Trip
DM switch 1 off
DM switch 2 off
DM confirmation on
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
ON
A

## Slide 27
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channel A+B+C Trip
DM switch 1 off
DM switch 2 off
DM confirmation on
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
ON
A

## Slide 28
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channel A+B+C Trip
DM switch 1 or 2 not off (perhaps on)-> actuator trip
DM confirmation on
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
OFF
A

## Slide 29
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channel A+B+C Trip
DM switch 1 or 2 not off
DM confirmation off
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
TRIP
MEM
OFF
A

## Slide 30
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
Maintenance/operation switch on
R
R
S
B
C
A
TRIP
MEM
ON

## Slide 31
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
OP push “Safe Stop” button in MCR -> causing actuator trip
Maintenance/operation switch on
R
R
S
B
C
A
TRIP
MEM
OFF

## Slide 32
TRIP
MEM
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
OP release “Safe Stop” button in MCR
.. Trip mem at once ready for reset
Maintenance/operation switch on
R
R
S
B
C
A
OFF

## Slide 33
OFF
R
2oo3
DM
OR
Safe Stop
AND
Operation mode
By-pass
AND
AND
Channels ok
DM switches on (towards target)
DM confirmation switch off
Safe stop ok
OP execute “Actuator Reset”
.. Actuator ready for “Start command”
Maintenance/operation switch on
R
R
S
B
C
A
TRIP
MEM