## Slide 2: 1. Updates on SPL Project
Rossana Bonomi
Rossana.Bonomi@cern.ch

## Slide 3: Outline 1.
SPL Project
Status Update
3
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014

## Slide 4: Aim of the SPL SCM study
What
  Design/construction/test of short version of Superconducting Cryomodule for High Power Proton beam (SCM)
Why
  For testing of 704 MHz superconducting cavities
When
  SCM is foreseen to be built and tested in 2014-2015
Where
  Design/production shared btw CERN, CEA, CNRS and industry
  To be tested at CERN, SM18
4
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014

## Slide 5: Main actors
5
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
System/Component/Activity | Person(s) in charge | Lab
Cavities/He vessel/tuner construction | O. Brunner O. Capatina T. Renaglia F. Pillon N. Valverde I. Aviles G. Devanz | CERN CERN CERN CERN CERN/ESS CERN/ESS CEA-Saclay
SRF, magnetic shielding, Clean-Room activities, RF test stations (SM18) | T. Junginger K. Shirm J. Chambrillon O. Brunner | CERN CERN CERN (formerly) CERN
RF Power Coupler | E. Montesinos, G. Devanz | CERN CEA-Saclay
Vacuum systems | G. Vandoni | CERN
Cryogenics (cryo infrastructure SM18) | O. Pirotte R. Van Weelderen | CERN CERN
Survey and alignment | P. Bestmann | CERN
Cryo-module conceptual design | R. Bonomi O. Capatina P. Coelho V. Parma D. Perez A. Vande Craen W. Zak | CERN/ESS CERN CERN/ESS (formerly) CERN CERN (formerly) CERN CERN/ESS
Cryo-module detailed design & Integration & Cryostat assembly tooling | P. Dambre P. Duthil P. Duchesne S. Rousselot D. Reynet | CNRS/IPNO-Orsay CNRS/IPNO-Orsay CNRS/IPNO-Orsay CNRS/IPNO-Orsay CNRS/IPNO-Orsay
SPL Machine architecture | F. Gerigk | CERN
ESS Cryomodule developments | C. Darve | ESS
Cryo-module Technical Coordination | V. Parma | CERN

## Slide 6: SPL Short Cryomodule
6
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
4 MW beam power accelerated up to 5 GeV
Half-length cryomodule (4 cavities) representative of full-length high power S.C. linac

## Slide 7: Status
7
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
SC Cavities
Design: CERN
Production: 5-cells, 1-cell in Nb and Cu produced by CERN and industry
He tank
Design: CERN
Production: Industry (CEA)
Mag. Shield
Design: CNRS (CERN spec)
Production: Industry
RF Power Coupler
Design: CERN (BE-RF, TE-MSC)
Production: CERN
Test: CEA (He, RF); CERN (N2)
Intercavity supports
Design: CERN
Production: CERN
Test: CERN (N2)
Vacuum vessel
Design: CNRS
Production: Under procurement
(construction before April 2015)
Tuner
Design: CEA
Production: CEA

## Slide 8: Time Schedule from Roland’s presentation
8
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Cryomodule assembly in 2015
..Test 2015 !

## Slide 9: 2. SPL Mock-up: Thermo-Mechanical Measurements
Rossana Bonomi
Rossana.Bonomi@cern.ch

## Slide 10: Outline 2.
SPL Supporting System
Test: Aim, Implementation
Methodology
Thermal Results: Comparison Test - Theory
Comments on Thermal Results
Mechanical Results
..Towards Helium
10
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: The outline of my talk ..

## Slide 11: SPL Supporting System
Features
  External conductors of main RF couplers (DWT)
  + Intercavity-supports (ICS)
  => No space frame, no rods
Requirements
  Allow for longitudinal and transverse thermal contractions
  Ensure low heat loads to the cold mass => Active gas cooling of DWT
11
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: recall on the SPL supporting system:
As seen in the previous presentation, the cavities in the spl machine are not supported by traditional space frames or rods: in order to lower the heat loads, we’ve been used some components which are already existing in the machine meaning the outer conductor of the main couplers and the intercavity supports.
Beyond the the stringent requirements on heat loads, this supporting scheme needs to cope with the unavoidable movements appearing during cool down.

## Slide 12: Test
Aim of the test
  Proof of theoretical studies concerning thermo-mechanical aspects of SPL supporting system
  Proof of alignment system
Implementation
  Full-size mock-up with “fake” cavities, 2 real DWTs and 1 ICS, inserted in vacuum vessel
  Cooled by LN2 and GN2
  No RF power
12
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: What is the test on the mockup for ?
Scope of the test is ..
How has it been implemented ?
Through a full size…..

## Slide 13: SPL Mock-up
13
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
.. Rendez-vous at SMI2 (b. 3191) tomorrow !
Sensors
  29 Thermal sensors: Pt100 and Thermocouples
  (23 Internal + 6 external)
  Mechanical sensors: displacements and bending
Notes: Nice picture of the installed mockup ..
Thermal and mechanical sensors (Pt100,thermocouples, bending and displacement sensors) have been placed on the mockup for experimental validation of theoretical studies regarding thermal performances and mechanical contractions.
ich you’ll discover tomorrow if you’re coming to the visit in SMI2.
Pt100 (class B) accuracy: <+- 1 deg
TC type E accuracy: < +-2 deg

## Slide 14: Methodology
Test: measurements * + postprocessing
Semi-analytical model for DWT temperature profiles and exchanged powers
FE thermal analysis (+ fluid dynamics)
Material-GN2 properties: Cryocomp, Gaspak
14
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
* 1 Hz acquisition frequency, 15 weeks of testing from October 2013 (overall).
Notes: The approach which has been adopted in general:
Get some measurements from our test by reading out of sensors (so far about overall 15 weeks of testing with 1 Hz acquisition freq).
Compare experimental data to both
analytical models already presented in my previous presentations (not giving here the details)
And to finite elements studies mostly thermal and with fluid dynamics calculations when needed.
Material and gas properties have beeen calculated with the cryocomp and gaspak sotwares.

## Slide 15: Mock-up: T Distribution
Test results, typical *
  No gas flow, steady state, cavities filled with LN2
288 K
(10 W)
15
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
77 K
103 K
93 K
80 K
77 K
77 K
77 K
147 K
207 K
256 K
* Data from April 2014.
Notes: Lets start from a typical temp distribution obtained last month during the test:
Cavities were kept cold, whereas dwt were not actively cooled
For example, we can highlight the t distrib obtained for the ics and for the dwt => ..

## Slide 16: DWT – No GN2 Cooling
Comparison with analytical and FE models
  No gas flow, steady state, fixed boundary temp
16
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Chart: x [m]
| 0 | 8.4000000000000005E-2 | 0.14899999999999999 | 0.214 | 0.3
TEST | 77 | 147.3333 | 207.1667 | 256 | 288
MATHCAD | 77 | 150 | 196 | 237 | 288
ANSYS | 77 | 149.455 | 201.42 | 245.01 | 288
Heater power Manually set * :
10 W
Estimated:
~10 W
~10 W
+3 deg
+2 deg
-11 deg
-6 deg
-19 deg
-11 deg
288 K
(10 W)
147 K
256 K
207 K
x
x
Temperatures
Good agreement at cold
Heater power
Very good agreement
* Data from April 2014.
Notes: Coming to the dwt, the most delicate component, during similar test conditions we obtained this temp distrib (on the left)
which is compared to that coming from estimations, both semi-analytical and fe models (on the right).
..Remind that no gas cooling is present !
So temp profile along the wall, from the cold bath to the outer flange which is being heated by a resistive wire is shown, and temp differences from test to theory are indicated. Red dots is the test results, blue and green are for fe and semi-anal values.
Despite bigger differences at warm temp, we are able to very well estimate temp profile at cold, which is the most important region as it is directly related to the heat flowing to the bath.
In fact, there is also good agreement f.w.c. heating power (around 10W).

## Slide 17: Mock-up: Static Loads
Conduction load through DWT is a major concern
Test results
  From DWT T profile, estimation of heat load (conduction) to cryogenic bath through each DWT: >10 W
  This value is in agreement with analytical estimations
  => For heat load reduction, active gas cooling of DWTs is necessary !
17
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: conduction load from the dwt is a driving load.
From the already shown temp profile obtained during the test when dwt is not gas cooled, we can say that more than 10 W are expected to reach the cryogenic bath in each dwt.
Therefore, it is imperative the introduction of gas cooling of dwt if we want to reduce static loads to the machine !

## Slide 18: DWT – GN2 Cooling *
18
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Chart: 5 ln/min (104 mg/s) @ 84 K
| 0 | 8.4000000000000005E-2 | 0.14899999999999999 | 0.214 | 0.3
TEST | 77 | 89 | 133 | 204 | 282
1.0bara | 77 | 97 | 128 | 177 | 282
ANSYS | 77 | 94 | 121 | 175 | 282
Chart: 7 ln/min (146 mg/s) @ 114 KTitle
| 0 | 8.4000000000000005E-2 | 0.14899999999999999 | 0.214 | 0.3
TEST | 77 | 113 | 150.5 | 207.5 | 276
1.0bara | 77 | 95 | 119 | 165 | 276
2.5bara | 77 | 94 | 118 | 164 | 276
ANSYS | 77 | 101 | 123 | 166 | 276
Chart: 10 ln/min (208 mg/s) @ 90 K
| 0 | 8.4000000000000005E-2 | 0.14899999999999999 | 0.214 | 0.3
TEST | 77 | 104 | 133 | 191.5 | 291.5
1.0bara | 77 | 86 | 103 | 148 | 291.5
ANSYS | 77 | 90 | 104 | 145 | 291.5
Chart: 12 ln/min (250 mg/s) @ 84 K
| 0 | 8.4000000000000005E-2 | 0.14899999999999999 | 0.214 | 0.3
TEST | 77 | 89 | 110 | 167.5 | 281
1.0bara | 77 | 83 | 94 | 132 | 281
ANSYS | 77 | 88 | 110 | 156 | 281
CASE 1
CASE 2
CASE 3
CASE 4
20 deg
* x-axis: x [m]; y-axis: T [K]. Pt100 accuracy: < ±1 deg. Data from various days in April 2014.
Temperatures
Good agreement at cold and fully developed steady conditions
Notes: Here you have the most representative results obtained with a gas cooled dwt. Also the inlet gas temp has been indicated.
They are plotted together with the theoretical predictions, which are based on fe and analytical studies. Again, in red and dots is the test, blu and green are for semi-analytical and fe results.
..

## Slide 19: DWT – Exchanged Powers *
19
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Chart: Q bath [W] vs GN2 flow [mg/s]
| 0 | 104 | 146 | 208 | 208 | 208 | 250
TEST-fromTprofile | -9.6457 | -1.6457 | -4.9371 | -3.0171 | -3.5657 | -3.7029 | -1.6457
MATHCAD-fromBalance | -10.5 | -2.4 | -6.1 | -2.2 | -2.2 | -2.7 | -1.7
ANSYS-react | -13.2 | -2.5 | -6 | -3.3 | -2.9
Chart: P heater [W] vs GN2 flow [mg/s]
| 0 | 104 | 146 | 208 | 208 | 208 | 250
TEST-set | 10.2273 | 27.2727 | 17.0455 | 27.2727 | 44.3182 | 40.9091 | 40.9091
MATHCAD-fromBalance | 9.7 | 26.3 | 29.6 | 40.1 | 46.1 | 43.6 | 48
ANSYS-react | 10.4 | 26.4 | 29.1 | 43.4 | 37.4
TRANSIENT NOT OVER
(cases 2, 3)
* Pt100 accuracy: < ±1 deg; Thermocouple type E accuracy: < ±2 deg. Data from various days in April 2014.
Tgas,in = 84 K 114 K 90 K 84 K
NO GAS COOL
Heater Power
Good agreement for fully developed steady conditions; Increases with flow
Heat to Bath
General good agreement; Small loads already with low flows;
Strongly depends on gas T at inlet

## Slide 20: Comments on Thermal Results
General nice agreement when steady state conditions are realized
Discrepancies can be due to
  Transients not completely over (DWT, flanges, gas temp)
  Limited n. of sensors for DWT temp profile
  Not shielded DWT sensors (vessel radiation)
  2-phases flow
  ..
20
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: …..

## Slide 21: Mechanical Measurements *
No constraints appearing on ICS during cool-down
Max displacement between cold cavities: ~4 mm, as expected
Max bending stress measured on DWT: 20 MPa, correspondent to expected friction in ICS
21
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
* Measurements from October-November 2013.

## Slide 22: Improvements / Next Steps
Improvements already adopted
  Improved gas line (insulation, bypass, T sensor)
  Separated dewar for GN2 extraction
  Insulated target supports (avoid condensation)
Modifications proposed for next tests
  Increase number of thermal sensors on DWTs for better accuracy
  Flowmeter on vent line for accurate heat load measurement and direct DWT load estimation
  Better insulation for heaters
  Better thermalization for masses (to reduce transients)
  Phase separator inside the vessel for GN2
  ..
22
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014

## Slide 23: ..towards Helium
Gas cooling is the most efficient solution
  2x electric power of ideal case (self-sustained wall cooling)
  this factor is 3x/6x for 2/1 ideal, optimized heat intercepts along the DWT wall
Estimation of mass flow required (100-300 mg/s N2 => 20-60 mg/s He)
Closed circuit (gas recovery, liquefier)
Easier regulation of gas temperature
..
23
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014

## Slide 24
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Thank you !
Acknowledgements
Alain Bastard
Patrick Bestmann
Ofelia Capatina
Cedric Charrondiere
Paulo Coelho
Jean-Baptiste Deschamps
Laetitia Dufay
Florian Girardot
Didier Gonnard
Alain Grimaud
Andre Guimet
Michael Guinchard + team
Torsten Koettig
Claudia Parente
Vittorio Parma
Eric Rasoasehno Michel
Michel Souchet
Arnaud Vande Craen
Wojciech Zak
Nicolas Zelko
SPL workspace
https://espace.cern.ch/spl-cryomodule/default.aspx
SPL docs on EDMS
https://edms.cern.ch/nav/P:SLHC-000008:V0/P:SLHC-000076:V0/TAB3

## Slide 26: Thermal Sensors
T1
T2
T3
T5
T4
T16
T17
T18
T20
T19
T6
T7
T21
T22
T23
T8 – T12
T9 – T13
T10 – T14
Int.
T11 – T15
Int.
T26
T27
Int.
T24
T25
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Notes: Overview of thermal sensors
Only inner ones are shown here and are distributed all over the mock/up
The external ones are those used for the flanges and fluid temperatures

## Slide 27: Tests foreseen
Test Program as of 10/2013

## Slide 28: Double-walled tube
Copper layer accounts for 5-7% of tot heat conducted

## Slide 29: Thermodynamic efficiency of DWT gas cooling
(Figure from: « An Introduction to Cryogenics », Ph.Lebrun, CERN/AT 2007-1)
He refrigeration He Liquefaction
How to compare isothermal and non-isothermal processes ?
Electrical power for liquefaction of 1 g/s helium: 6200 Wel
Carnot COP @ 4.5 K: 66 Wel/Wth
1 g/s liquid helium is equivalent to 100 Wth @ 4.5 K *
* U. Wagner s note:
http://cdsweb.cern.ch/record/808372/files/p295.pdf

## Slide 30: Thermodynamic efficiency of DWT gas cooling
Comparison with other ways of cooling (heat intercepts, self-sustained cooling)
990 @ 2 K, 220 @ 4.5-9 K, 16 @ 80 K
Case | Q @ 2K [W] | P [Wel] | Q @ 9K [W] | P [Wel] | Q @ 80K [W] | P [Wel] | Flow rate [g/s] | Q equiv. @ 4.5K [W] 1g/s=100W | P [Wel] | Total power [Wel] | 
A) No intercept | 12.6 | 12,375 | - | - |  |  | - | - | - | 12,375 | 26.3
B) 1 optimised intercept @ 80K | 2.2 | 2,178 | - | - | 44.6 | 714 | - | - | - | 2,892 | 6.1
C) 2 optimised intercepts @ 80K & 9K | 0.18 | 178 | 3.2 | 704 | 30.6 | 490 | - | - | - | 1,372 | 2.9
D) 4.5K self-sustained vapour cooling | 0.03 | 30 | - | - | - | - | 0.020 | 2 | 440 | 470 | 1
E) He vapour cooling (4.5K-300K) | 0.10 | 99 | - | - | - | - | 0.040 | 4 | 880 | 979 | 2.1
F) He vapour cooling (4.5K-300K), RF power on | 0.50 | 495 | - | - | - | - | 0.040 | 4 | 880 | 1,375 | 
G) No He vapour cooling, RF power on | 22 | 21,780 | - | - | - | - | 0 | 0 | 0 | 21,780 | 

## Slide 31: Mock-up: Static Loads
FE model
  No gas flow, steady state, warm MLI surface*
Typical value of radiative heat load on cold cavities (wrapped by 30 layers of MLI) is confirmed: 1-2 W/m2
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
TMLI* [K] | εMLI | TVV [K] | εVV | QRAD,ANALYT [W/m2] | QRAD,ANSYS simple [W/m2] | QRAD,ANSYSreal [W/m2]
290 | 0.02 | 300 | 1.00 | 1.2 | 1.7 | 1.2
290 | 0.02 | 300 | 0.20 | 1.1 | 1.6 | ..
* MLI surface temperature calculated with mli.exe [Chorowski]

## Slide 32: Intercavity Support
Comparison with FE model
  No gas flow, steady state, cavities filled with LN2, radiation with 300K vessel
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
103 K
93 K
80 K
110 K
100 K
85 K
Good agreement with estimations

## Slide 33: 16/4/2014, 21:00 (45000s) -1 hr shift in daq
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
5 ln/min (104 mg/s) @ 84 K
80 V (27 W)

## Slide 34: 16/4/2014, 12:00 (9600s) -1 hr shift in daq
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
7 ln/min (146 mg/s) @ 114 K
50 V (17 W)

## Slide 35: 16/4/2014, 15:00 (20000s) -1 hr shift in daq
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
10 ln/min (208 mg/s) @ 87 K
80 V (27 W)

## Slide 36: 16/4/2014, : (s) -1 hr shift in daq
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
12 ln/min (250 mg/s) @ 84 K
80 V (27 W)

## Slide 37: 16/4/2014
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014
Chart: GN2
Chart: 
| 13.308999999999999 | 13.285 | 13.279 | 13.266 | 13.279 | 13.246 | 13.295999999999999 | 13.27 | 13.257 | 13.260999999999999 | 13.263 | 13.272 | 13.285 | 13.268000000000001 | 13.276 | 13.268000000000001 | 13.265000000000001 | 13.260999999999999 | 13.246 | 13.255000000000001 | 13.255000000000001 | 13.255000000000001 | 13.244 | 13.247999999999999 | 13.244 | 13.238 | 13.250999999999999 | 13.25 | 13.260999999999999 | 13.246 | 13.234999999999999 | 13.233000000000001 | 13.221 | 13.233000000000001 | 13.202 | 13.228 | 13.239000000000001 | 13.241 | 13.217000000000001 | 13.225 | 13.173999999999999 | 13.214 | 13.239000000000001 | 13.201000000000001 | 13.177 | 13.172000000000001 | 13.153 | 13.145 | 13.163 | 13.196999999999999 | 13.173999999999999 | 13.217000000000001 | 13.153 | 13.2 | 13.169 | 13.156000000000001 | 13.147 | 13.137 | 13.145 | 13.147 | 13.124000000000001 | 13.141 | 13.114000000000001 | 13.138 | 13.135 | 13.144 | 13.151999999999999 | 13.164999999999999 | 13.166 | 13.144 | 13.154999999999999 | 13.154999999999999 | 13.163 | 13.151999999999999 | 13.153 | 13.163 | 13.178000000000001 | 13.185 | 13.204000000000001 | 13.183 | 13.166 | 13.163 | 13.166 | 13.159000000000001 | 13.144 | 13.161 | 13.15 | 13.148 | 13.135 | 13.138 | 13.137 | 13.15 | 13.17 | 13.163 | 13.176 | 13.167999999999999 | 13.194000000000001 | 13.209 | 13.201000000000001 | 13.209 | 13.183 | 13.173 | 13.17 | 13.162000000000001 | 13.173 | 13.157 | 13.157 | 13.164 | 13.202999999999999 | 13.2 | 13.189 | 13.167999999999999 | 13.161 | 13.192 | 13.186 | 13.201000000000001 | 13.183999999999999 | 13.196 | 13.191000000000001 | 13.205 | 13.201000000000001 | 13.193 | 13.185 | 13.179 | 13.191000000000001 | 13.211 | 13.221 | 13.206 | 13.198 | 13.183 | 13.186999999999999 | 13.193 | 13.180999999999999 | 13.172000000000001 | 13.167999999999999 | 13.207000000000001 | 13.183999999999999 | 13.207000000000001 | 13.183999999999999 | 13.214 | 13.223000000000001 | 13.205 | 13.176 | 13.172000000000001 | 13.186 | 13.172000000000001 | 13.191000000000001 | 13.167999999999999 | 13.144 | 13.135999999999999 | 13.148999999999999 | 13.132999999999999 | 13.135999999999999 | 13.118 | 13.112 | 13.11 | 13.101000000000001 | 13.084 | 13.097 | 13.082000000000001 | 13.086 | 13.102 | 13.112 | 13.095000000000001 | 13.085000000000001 | 13.112 | 13.106 | 13.135999999999999 | 13.145 | 13.122 | 13.153 | 13.180999999999999 | 13.127000000000001 | 13.164 | 13.119 | 13.138 | 13.122999999999999 | 13.164 | 13.138999999999999 | 13.127000000000001 | 13.101000000000001 | 13.095000000000001 | 13.112 | 13.1 | 13.138999999999999 | 13.124000000000001 | 13.096 | 13.109 | 13.109 | 13.069000000000001 | 13.071 | 13.067 | 13.073 | 13.093 | 13.095000000000001 | 13.097 | 13.112 | 13.118 | 13.105 | 13.101000000000001 | 13.108000000000001 | 13.108000000000001 | 13.097 | 13.11
Alarm 203

Alarm 204
Alarm 205
7 ln/min (146 mg/s) @ 114 K
50 V (17 W)
12 ln/min (250 mg/s) @ 84 K
80 V (27 W)
10 ln/min (208 mg/s) @ 87 K
80 V (27 W)

## Slide 38: Tgas,in vs Qbath
Chart: 
| 0 | 104 | 146 | 208 | 208 | 208 | 250
T gas [K] | 0 | 84 | 114 | 87 | 87 | 90 | 84
abs(Qc x 10) [W] | 96.4571 | 16.4571 | 49.3714 | 30.1714 | 35.6571 | 37.0286 | 16.4571
R. Bonomi TE-MSC-CMI
SLHiPP-4, CERN 15-16/5/2014