## Slide 1
ESS Cooling and
Heat Recovery system
Thomas Hjern
Design Leader Process systems
Conventional Facilities
EuCARD-2 Lund April 28, 2014

## Slide 2
System design
  General energy design concepts
  ESS design basis for heat recovery
  Cooling water distribution system
  Heat sinks for heat recovery
  Heat recovery system
Lessons learned – so far
      Overview

## Slide 3
Design for low energy consumption
“Protect” high temperatures
Look for existing and potential heat sinks
      General energy design concepts

## Slide 4
Heat Recovery included from start of design!
All energy applications designed for heat recovery
  Use highest possible cooling water temperature
  Give highest possible return temperature
  Low pressure drop
Three cooling water temperature levels
  Low: 10°C = lowest required temperature
  High: 50°C = lowest temperature without heat pumps
  Mid: 25°C = “optimum” mid-temperature
      ESS design basis for heat recovery

## Slide 5
      Cooling water distribution system
Site wide
distribution
All supplies
9 bar g!
All returns
6 bar g!
CW return
<30⁰C
CW return
30-50⁰C
CW supply
50⁰C
PC
CW supply
25⁰C
PC
CW supply
10⁰C
PC
Cooling
&
Heat Recovery
CW return
>50⁰C
Central Utilities Building (CUB)
Cooling loads
If
30-50°C
If
>50°C
If
>50°C

## Slide 6
Existing municipal District Heating (DH)
  Warm supply 80°C
  Cold return 45°C
New Low Temperature District Heating (LTDH)
  Warm supply 55°C
  Cold return 25°C
  ESS internal district heating
  Science Village?
  Greenhouses?
  New municipal areas?
      Heat sinks for heat recovery

## Slide 7
      Heat recovery system
CW-L
Buffer
tank
150m3
CW-M
Buffer
tank
150m3
CHILLERS
HEAT PUMPS
CW return
<30⁰C
CW return
30-50⁰C
CW supply
25⁰C
CW supply
10⁰C
CW supply
25⁰C
CW return
30-50⁰C
DH
DH
Backup
air cooler
CW supply
50⁰C
CW return
>50⁰C
DH
DH
Backup
air cooler
LTDH
cooler
LTDH
cooler
”Balance
flow”
”Balance
flow”
12 MW
17 MW
4 MW
COPh
3,6
COPh
5,6

## Slide 8
Large potential for energy optimization in design stage
  “Half cost, double profit” compared to later modifications
Integrated design from “klystron to district heating”
  Machine designers and scientist not used to consider heat recovery
  Energy management must be a top management priority
  Avoid subsystems
Important to have a Life Cycle Cost focus
  Project management must focus on operating cost
Think more industry – Less laboratory!
      Leasons learned – so far

## Slide 9
Thank you!