## Slide 1: Target Safety System (TSS) Status TAC9
Linda R. Coney
Group Leader – Target Safety and Controls
www.europeanspallationsource.se
April 2-3, 2014

## Slide 2: Outline
Intro – TSS objectives & functions
TSS description & plan for development
Risk (Hazard) Analyses
  Procedure & Progress
ICS/Target Interface
  MPS, PPS, and Standard Controls
Conclusions

## Slide 3: TSS – Purpose
TSS is a safety critical system designed to protect the public and environment from radioactive release
Active control and monitoring system
  It is likely that the TSS will need to be able to shut down the proton beam
  Actions not necessarily limited to beam shut down
Safety-certified system
  Essential to the certification process for the ESS
  Working closely with the ES&H group on requirements

## Slide 4: ESS Control Systems – Objectives
TSS - Limit transfer of radioactive contamination to the public, workers, and environment
PSS - Suppress radiologic hazards by switching off the proton beam
  Control access to restricted areas during operations
MPS – Protect investment from damage due to beam losses and malfunctioning equipment
  Optimize integrated machine performance
  Stop beam – Beam Interlock System
TSS – Independent safety-qualified system
g Not tied into other I&C systems
Personnel Safety System

## Slide 5: TSS – Link with ESS Safety Concept
As described in the ESS PSAR (ESS-02), there are several physical confinement barriers to limit radiological impact on the environment in accordance with the ESS GSO
  Target Wheel, Monolith, & Building
TSS is an active safety barrier – potential actions may include
  Stop energy production g p+ beam shut down
  Evacuate stored energy
  g After heat management
  g Evacuate H2 inventory
  Confine radioactive material
  g Isolation of some active circuits
  g Dynamic confinement
3rd confinement barrier: TS building
1st confinement barrier: target circuit
2nd confinement barrier: monolith liner

## Slide 6: TSS – Preliminary Top Level Requirements
Single failure criterion:
  Redundancy, physical separation adapted to different aggressors (zoning)
  Independence, electrical isolation
Fail-safe principle
  Safe state must be clearly identified
  Loss of power g actuators default to safe position
  Actuator commands ‘de-energize to trip’
Emergency power supply coverage
Qualified for extreme operating conditions g seismic classification for a subset of functions
No requirement on post-trip machine availability
  Contrasts with MPS (Machine Protection System) – non-safety system designed to monitor machine parameters, shut down beam, and allow quick turn-around

## Slide 7: TSS – Description
Applying top level requirements g initial design concepts
  Two independent shutdown mechanisms to stop beam
    Ion source and RFQ – details not yet defined
    Direct access/priority to shutdown mechanisms
  Use safety-rated PLCs
  Two separate TSS rooms in Target building
  Independent paths to each beam shut-off system
  Separate from ICS controls – cable-trays, UPS, shutdown mechanisms
  Additional target-specific controls – ex. He cooling system for target wheel, wheel motion, ventilation control
  Satisfy requirements & protect public with as-simple-as-possible system

## Slide 8: Plan for TSS Development
Risk Analyses 2013/2014
Description of TSS Logic 2014/2015
  MS: PDR of TSS Logic Definition April 2015
Design of TSS Architecture
  Includes documentation & safety analysis of system architecture
  MS: CDR of TSS System April 2016
Manufacturing Fall 2016 g Fall 2017
  Supplier chosen Nov 2016
  Delivery to site Fall 2017
Installation/Testing/Cold Commissioning g Early 2019

## Slide 9: TSS – Risk Analyses
Perform risk analyses for Target Station systems for TSS and MPS
  Define the system – understand what included in analysis, drawings, schematics, etc.
  Identify hazards – radioactivity, stored energy, explosion, impact (load drop), etc.
  Identify initiating events and top events – circumstances that would produce a hazardous situation
  Describe consequences if no mitigation
  Estimate probability and severity g unmitigated risk ranking
  Define applicable barriers – confinement & safety barriers and associated triggers
  Leads to Target Station system design recommendations & study recommendations
Qualitative Risk Analysis g mid-2014
  Target Station System Design & Study Recommendations for both TSS and MPS
  Inputs and outputs for TSS
  Start of TSS logic design
Feed information back into Quantitative Risk Analysis
  2014/2015 – PDR Spring 2015
Iterative process to accommodate modifications to design

## Slide 10: Risk Analyses: Target Station Components
Systems evaluated during Risk Analyses – including relevant primary fluid systems
  Cold Moderator
  Water Moderator
  Reflector
  Target (wheel, drive, He cooling system)
  Monolith
  PBW
Ventilation, Intermediate cooling systems, Remote Handling, Beam Dump
Instrumentation
  proton beam and target monitoring

## Slide 11: Risk Analysis – Risk Ranking
Categories for probability & consequences
Probability |  |  | 
H1 (Normal Operation) | Risk reduction recommended | Unacceptable | Unacceptable
H2 (Incidents) | Risk reduction recommended | Unacceptable | Unacceptable
H3 (Unexpected events) | Tolerable | Risk reduction recommended | Unacceptable
H4 (Design basis Accident) | Tolerable | Tolerable | Risk reduction recommended
Severity | Minor Damage | Moderate damage | Major damage
 | Non- radiation: mild symptoms, no remaining injury | Non- radiation: requires medical care, could give remaining injury | Non-radiation: possibility of death
 | Radiation: No increased radiation exposure, typically 0-1 containment barriers impaired | Radiation: significant uncertainty regarding outcome, but not expecting increased radiation exposure. Typically 1-2 containment barriers impaired | Radiation: increased radiation exposure. Typically 2-3 containment barriers impaired.

## Slide 12: Risk Analysis – MPS & TSS Example Cold Moderator
 | Protection/safety Barriers | Triggers | Design barriers/Recommendation | Recommendations for studies and investigations | Comments
MPS | Automatic shutdown of proton beam. Evacuation of H2 from Monolith atmosphere, Isolation of He purification unit | Low pressure (L threshold) in H2, High pressure (H threshold) in Monolith He | R: provide mechanical limiters to protect the accumulator bellows from being destroyed; | R: Analyze LH2 cold shock on the target vessel to demonstrate that it does not break; R: Analyze LH2 cold shock on the water vessels (therm mod and reflector, shielding) to demonstrate they do not break R: estimate the pressure resulting from LH2 vaporization into Monolith; | we assume the circulators can run without LH2, at least for a short time;
TSS | Automatic shutdown of proton beam. Evaucation of H2 from Monolith atmosphere, Isolation of He purification unit | Low pressure (LL threshold) in H2, High pressure (HH threshold) in Monolith He | R: safety credited relief valves into expansion volumes shall be considered in the design; | R: estimate the pressure resulting from LH2 vaporization into Monolith - check whether H2 is under or above 4% vol.; R: estimate the potential radiological impact coming from the purification system; | if H2 is less than 4% in the monolith Helium only, then there is no H2-barrier to consider anymore;
System of concern | Protection/safety system | Preliminary Initiating Events (PIE) | Top Event | Unmitigated Consequences | Probability | Severity | Risk Ranking
Cold Moderator | MPS | Mechanical failure. Structural problem of the circuit itself. Mechanical stresses (temperature changes ex. Start-up/shut-down). Irradiation damage to material. Circuit pump failure + External aggressor (dropped mass) | M.1.3.4 H2 rupture including vacuum lines: leak into He (monolith) | cold shock to some equipment; cryogenic conditions not maintained. Could lead to rupture cold moderator vessel nearby the wheel due to lack of coolant in it. Pressure increase in the He Monolith circuit up to XXX. Saturation of He purification system. | Exceptional | Catastrophic | 
Cold Moderator | TSS | Mechanical failure. Structural problem of the circuit itself. Mechanical stresses (temperature changes ex. Start-up/shut-down). Irradiation damage to material. Circuit pump failure + External aggressor (dropped mass) | T.1.3.4 H2 rupture including vacuum lines: leak into He (monolith) | loss of 1 H2-barrier between H2 and air. Cold chock to some equipment; Could lead to rupture in the cold moderator vessel nearby the wheel due to lack of coolant in it. Pressure increase in the He Monolith circuit up to XXX which could lead to monolith rupture. Saturation of He purification system. | H4 | Moderate | 

## Slide 13: Risk Analysis Status
Completed qualitative RA for:
  Water Moderator, Cold Moderator, Reflector
Currently working through Target system RAs
  includes Target wheel, drive, He cooling circuit & He purification
Next: Proton Beam Window (PBW)
Following:
  Monolith, Active Gaseous Storage, Ventilation, Remote Handling, Process Cells, All Intermediate Cooling Circuits, Beam Dump
Revisit first systems in Quantitative RA starting in May
Developing procedure to track & document incorporation of design recommendations and study results

## Slide 14: Target Controls – ICS Control Systems
Machine Protection System (MPS)
  Optimize operational efficiency, machine availability, & reliability
  Requirements
    Stop the proton beam in case of failures
    Prevent damage to elements in the accelerator & target
    Provide tools for failure-tracing throughout machine
  Objectives
    Protect the machine
    Protect the beam – avoid unnecessary beam-stops
Personnel Safety System (PSS)
  Protect personnel against unnecessary exposure to hazards from the machine, including radioactivity and electromagnetic radiation
  Support multiple operational modes of facility
  Primarily access control & radiation monitoring and alarm systems
ICS – other instrumentation and controls

## Slide 15: Relationship Between TSS – MPS – ICS

## Slide 16: MPS - Target
Beam Interlock System (BIS)
  Terminates beam production when failure detected
  Establishes a global BEAM PERMIT
  Determines permissible operational modes
    Machine configuration + beam parameters
    Fast response-time system – 10 msec
    Sensors – BLMs, BCMs, BPMs
  Response for slower time-scale sensors & systems < 70 msec
BIS for Target
  Time scale of response ~100msec
  Ongoing Risk Analyses will provide information on input
    Ex. Movement of target wheel – position synchronized with proton beam arrival
  Preliminary example:
    Input signals for Target Slave as part of Beam Interlock System
    Beam Permit given if all conditions met

## Slide 17: PSS - Target
Preliminary requirements/design discussions under way
Controlled access systems for rooms next to target station (red) on all floors
  Beam off triggered
Remote Handling galleries/Maintenance cell area require access control tied to radiation monitoring
  Not tied to accelerator operations or beam interlock

## Slide 18: TSS – Conclusions
The process to derive the set of TSS controls has been developed and is well under way.
  Understand TSS purpose within overall ESS safety plan & define TSS requirements
  Execute Risk Analyses – derive target station system design requirements, initiate necessary studies, & define TSS logic
  Build description of TSS architecture and finalize design
Final TSS system design is planned for 2016.
Frequent coordination continues with ES&H and ICS groups to ensure proper interfaces exist for TSS and Target MPS.