## Slide 1: Cooling ESS
Anton Lundmark
Cooling System Engineer
www.europeanspallationsource.se
10 December 2014

## Slide 2: Outline
Scope
Design objectives
CUB
Accelerator
Target
NSS

## Slide 3: What are the different scopes?
NSS design teams
Target design teams
Accelerator design teams
“Work package 16”
CW requirement coordination
CW interface to “machine” Contaminated CW systems
Local CW systems
CF Process
Cooling Water production (CUB)
Site distribution
Main headers in buildings
Heat recovery systems
CF HVAC
Heating
Cooling
ESS Energy Team
District Heating

## Slide 4: Design objectives
Reliability “..never cause shutdown of accelerator..”
Availability 6500 hours per year at full load
“..never have total CW shutdown..”
Stability Supply temperature +/- 1 °C
Supply pressure +/- 0,1 bar
            Flexibility Wide operating range
Design margins for critical components
Recycling Recover waste heat
Responsible High energy efficiency

## Slide 5: CUB Process Layout

## Slide 6: Process piping – main distributiuon
CUB
expansion
area
Process piping in ground
1 m box culvert (surface)
3 m underground piping
1 m future
To Campus area
G02-1
”HVAC” piping in ground
2 m underground piping
From CUB
D04 + D05
D04
D05
G02 + G04
G02-2
G02-3
Subst. 1
Subst. 2
Subst. 3
Logistic Center

## Slide 7: WP16 interfaces to Accelerator/Conventional facilities
Ion source
LEBT
RFQ
DTL
MEBT
Couplers
Couplers
HEBT
LWU
Klystron body
Kly. collectors
Amplifiers
Power supp.
Circulators
Load
LLRF
Helium cooler
Oil cooler
Motor cooling
Turbine breaker
Klystron body
Kly. collectors
Amplifiers
Modulators
Power supp.
Circulators
Load
LLRF
Central Utility Building
WP4
Spokes
WP5
Elliptical
WP6
Magnets
WP8
RF
WP10
T.S.
WP11
Cryo
WP3
NC linac
WP16
Cooling
WP17
Power conv.

## Slide 8: Front End Building

## Slide 9: RF Gallery

## Slide 10: Accelerator Cryoplant Cooling
Compr. motor
Middle temperature Return
Middle temperature Supply
Oil vessel
Helium compressor
Helium cooler
Oil
cooler
He to cold box
He from cold box
High temperature Return
Middle temperature Return
25C
25C
27C
27C
27C
39C
85C
85C
90C
32C
90C
32C
83C
37C

## Slide 11: NSS

## Slide 12: NSS Labs
Labs will have multiple components requiring cooling
  Reflectometers/diffractometers
  Furnaces
  Cryogenic refrigerators
  Electronic racks
  Etc.

## Slide 13: Target cooling systems
DO 00035
DO 00070
DO 00034
To Cryo cooling
CW High
return
CW Low
supply
CW Low
return
CF cooling system scope
Specialized Technical Services cooling scope
Target cooling scope

## Slide 14: Typical components

## Slide 15: ?
Questions?
If you have questions later, don´t hesitate to contact me!

## Slide 16: Thank you!