## Slide 2: SE Integration
Workflow and Solutions
Experiment Control and Data Curation (ECDC)
Anders Pettersson

## Slide 3: Agenda
1 NICOS High level control system
2 Different solutions Same User Experience same
3 Overview of SE integration
4 EPICS
5 Octopy
6 SE integration workflow
7 Summary

## Slide 4
NICOS
High Level Control System
1

## Slide 5: NICOS
  Instrument cabin
  User and Expert interface
  Qt based
  Extensible and customizable
All devices shall be available in NICOS
  Scripting
  Python CLI
  Plotting live data

## Slide 6: NICOS
  What signals to expose?
    Data
    User parameters
    Expert parameters
  Maybe not?
    Proprietary data evaluation software
    Low level hardware configuration parameters available in device software
Signals

## Slide 7
Different Solutions
Same User Experience
2

## Slide 8: Different solutions Same User Experience
EPICS
  Standard devices are straightforward to integrate and control in EPICS
  Robust
  Deployment supported by ICS under development
  Comes with software infrastructure like GUIs, Archiver, Save and Restore, etc
  Community integrations available
Use case: EPICS for standard systems

## Slide 9: Different solutions Same User Experience
  Not straightforward with EPICS
  Labview not supported by ICS
  ICS only supports Linux machines (DLL requires Windows)
  ”Normal” complexity with Octopy
  Octopy python based, runnable on most systems
Use case: Octopy for device requiring a DLL (potentiostat)
Notes: Octopy provide a solution where EPICS is limited

## Slide 10: Different solutions Same User Experience
  Octopy is SE’s tool with which to encapsulate SE low level complexity and expose a standard interface
  Configurations are modular and can be changed dynamically
  Leverages power of existing Python libraries
  Python scripts can be added in a modular way
  Logic accessible to SE staff (if familiar with Python)
Use case: Octopy Development systems Orange Cryostat, Rig1, LS336 Tctrl calib, Camera

## Slide 11: Different solutions Same User Experience
  Development of timestamping system
  PLC (Beckhoff) synchronize to ESS time through PTP
  Standard MQTT library is used for PLC to push data to Octopy -> EPICS
  Same setup is used in Rig1 project. PLC (cRio NI) with labview use MQTT library to push data to Octopy-> Epics
  The PLC + PTP approach provide solution for timeresolution 10-100us and sample rate 1-10ks/s
  Detector readouts can be used for higher resolution
Use case: Higher timestamping resolution

## Slide 12: Different solutions Same User Experience
  Translate a SECoP device to EPICS
  Develop a ESS SE system for SECoP
Use case: Octopy for SECoP Devices
Network

## Slide 13
Overview of SE integration
3

## Slide 14: Overview SE integration
The Sample Environment System
Communication over :TCP/IP, Serial, RS232, Etc..
A selection of commands defined in device manual
Information collected in JIRA issue
ESS Timing network
SEE
SE System
SEE

## Slide 15: Overview SE integration
The SES integration
EPICS Process Variables (PV)
Technical Network
EPICS
Octopy
ESS Timing network
SEE
SE System
SEE
Local IPC
Integration phase
Integrators setup communication with SE system
Implementation of requested logic
Notes: The integration ”coding” is provided either as ESS standard EPICS or in specific cases in Octopy , local SE control system

## Slide 16: Overview SE integration
Experiment Control System (ECS) and NICOS
EPICS
Octopy
NICOS
EPICS
forwarder
Kafka
Filewriter
NeXus/HDF5
ESS Timing network
EPICS Process Variables (PV)
Technical Network
SEE
SE System
SEE
Local IPC
User interface
Setup in NICOS
Data accessed by EPICS forwarder
Notes: Exposeing signals on EPICS enable access on ESS controls infrastructure

## Slide 17
EPICS
4

## Slide 18: EPICS
EPICS - Experimental Physics and Industrial Control System
  EPICS is the signal layer backbone at ESS
  Every remote controlled signal or data need to be available as an EPICS PV (Process Variable)
  All SE hardware is integrated into EPICS
  ICS WP12 provide integration working close with ECDC
  ECDC priorities NSS integration tasks
  All data will be timestamped in EPICS
Integrated Control Systems Division - ICS WP12
Notes: Open source facility control system/Scada system used at large research facilities (radio telescope array, telescopes, synchrotrons, Xfel etc).

## Slide 19: EPICS
  EPICS is also a collection of tools:
    Archiver
    CS-Studio (GUI)
    Alarm handling
    Save and restore
    Deployment system Etc..
    NB. Archiver not fully compatible with ESS EPICS, Save and Restore not tested, (3rd ) Deployment system under development)
EPICS additional Tools
Archiver
Alarm handler
CS-Studio

## Slide 20: EPICS
From SE perspective
CS-Studio Phoebus -> Engineering Interface (mainly SE team)
Troubleshooting/development interface
Archiver –> long term SE monitoring
Not the interface for the Science User
Potentially providing device hardware configuration parameters not exposed to User.
Will not provide scripting
CS-Studio Phoebus GUI, Archiver

## Slide 21
Octopy
5

## Slide 22: Octopy
  Local SE control system implementing SECoP
  Developed by Sample Environment for low level controls of a SES
  Meets the SE needs for flexibility and modularity
  Developed to be compatible with ESS EPICS infrastructure
  Allows addition of logic
  Can communicate with SECoP ECSs and will be able to translate SECoP devices to EPICS
  SECoP provides a self describing feature potentially reducing ECS integration effort
  Compatible with EPICS tools (in theory…)
Sample Environment Controls

## Slide 23: Octopy
Project status
Octopy SE development system:
  JULABO(sim) -> EPICS IOC -> Octopy -> EPICS
  Beckhoff PLC -> MQTT -> Octopy -> EPICS
  LakeShore336 -> TCP/IP -> Octopy -> EPICS
  Status:
  GUI for creating and editing of configurations
  Signals can be integrated/added from GUI
  CS-Studio Phoebus compatible
  Operational by summer
  Seamless integration with EPICS ecosystem still in progress

## Slide 24
SE Integration Workflow
6

## Slide 25: SE Integration Workflow
Workflow document
  SE integration workflow document
    Describes integration process
    Intended to help flow of information
    Adjustable to size of project

## Slide 26: SE Integration Workflow
Workflow
  STEP 1
  Client fills out the integration request template when a SE device is ready for integration
Notes: Trigger an integration project

## Slide 27: SE Integration Workflow
Integration Request
Client/subject matter expert provide
Clear information/scope
Integration reference
Catch safety considerations
Lists signals
Template evolved over multiple projects
Notes: MESI/ECDC can support

## Slide 28: SE Integration Workflow
Main phases
Stakeholder meeting
General description
Use cases
Required logic development
Project JIRA issue
Purpose:
Catch challenges early
Involve integrators
Meet!
Both side Q/A
Main Integration effort
Integration in ESS control systems
Purpose:
Enable remote control of SE by user
Enable writing experiment data
Project start
Purpose
Refine timeline
Prepare support
Engineering document
Document system/new logic
Purpose:
Provide clear description of new logic for integrator/developers
Reduce misunderstandings
Acceptance testing
Is the client happy?
Purpose:
Align that project is done
Notes: MESI supports projects on mechatronics and control.
ECDC supports in controls and interpretation of commands etc.
Design process can be iterative

## Slide 29: SE Integration Workflow
An integration requests triggers a new ECDC JIRA issue
Issues are prioritised for integration and queued into ICS sprints
NICOS integration starts as EPICS integration is finalized
The JIRA issue collects information and keeps stakeholders updated/involved
SE/ECDC/ICS interaction

## Slide 30: SE Integration Workflow
Individual SE systems and Sample Environment Systems
Indicative statistics, not fool-proof

## Slide 31
7
Summary

## Slide 32: Summary
  Functional workflow from Hardware to UI
  SE provide good input
  EPICS integrators positive to workflow
  Structure essential! (++ in Covid)
  Limited integration resources
  Situation will get worse over time, when more equipment (also non-SE) arrives and instrument installation begins – strong need to accelerate completion of projects
  Complementary integration solutions
  Octopy used by SE
    to build complete SES with internal logic
    expose a standard interface without involving ICS/ECDC in selection of hardware
  YMIR helps drive SE controls
  B02+E03 etc big step towards final structure

## Slide 33: Thank You for listening!