## Slide 1: ESS HPRF Distribution: Technology Enhancement for High Temperature RF Loads
Author: Rutambhara Yogi

## Slide 2
Suppliers:
Many thanks to
Colleagues:
ESS: David McGinnis, Anders Sunnesson, Morten Jensen, A. Johansson
Carlos Martins, Rihua Zeng, Rafael Montano, Chiara Marrelli,
Stevo Calic, Daniel Lundgreen, Carl Johan Hardh
FREIA: Rolf Wedberg, Lars Hermansson, Roger Ruber & other colleagues
CERN: Eric Montesinos, Olivier Bruner
SNS: Crofford Mark

## Slide 3
Overview:
ESS RF systems
Earlier plans for Load Cooling
Present plans for High Temperature cooling
Technology enhancement & New Developments
* Resistive Loads
* Ferrite ER Load
* Ferrite load (ferrite tiles)
* Water Load

## Slide 4
Klystron
84 High Beta cavities
704 MHz
New development: IOT
Backup solution: Klystron
26 Spoke Cavities,
352 MHz
400kWp
Tetrode
36 Medium Beta cavities
704 MHz
1.5MWp Klystron
1200 kWp
1500 kWp
Warm Linac
-1 RFQ & 5 DTL
352 MHz
3MWp Klystrons
-3 MEBT
352 MHz
30kWp Solid State Amplifiers
ESS HPRF Systems

## Slide 5
RF Loads
Isolator Load: Used with circulator to protect amplifier
To dissipate RF power during Amplifier testing
FAT at AFT
HB/MB Linac
Circulator
Load
Klystron
RF loads: Matched terminations
100 loads
Frequency = 704 MHz,
Power = 1.5 MWp
(Isolator loads)
Flow requirement:
70 lpm x 100

## Slide 6
Reject load: RF load with 3 dB Combiner (Hybrid coupler)
Reject
Load
Circulator
Hybrid
coupler
Isolator
Load
Courtesy: FREIA
52 Loads
352 MHz
Isolator loads:
400 kWp,
Qty: 26
Reject loads:
100 kWp,
Qty:26
Flow requirement:
30 lpm x 100
Spoke Section:

## Slide 7
12 Loads
352 MHz
Isolator loads:
3 MWp,
Qty: 6
Reject loads:
0.75 MWp,
Qty:6
Flow requirement:
135 lpm x 12
RF load with 3 dB Splitter (Hybrid coupler) as Reject load:
RFQ/DTL
Isolator
Load
Circulator
Klystron
(3 MWp)
Hybrid
coupler
Reject
Load
ESS needs 170 loads !
Huge load requirement
Huge flow requirement
Note-Layout is not finalized

## Slide 8
ESS will have three cooling circuits: 10oC, 25oC, 50oC
Loads were on medium temperature circuit ie. 25oC
Hot water
from Lund city
50oC
Heat Pump
50oC to 25 oC
Electricity
Medium temp
Water at 25 oC
Heat Pump
40oC to 80 oC
Loads
ΔT ≈ 1oC
To Lund
city
# Decided to have
loads on 50oC
cooling circuit
# Components shall
be in series without
affecting
Reliability.
Electricity
Hence technology enhancement !
Not energy efficient
Solution !
Earlier Plans for Load Cooling
Max load outlet
temperature:
40oC
80 oC

## Slide 9
Klystron
Load
Klystron
Load
N Number
HB / MB Linac
50oC
N Number
Outlet temp
Controlled to 60oC
Spoke Linac
N Number
N Number
50oC
Tetrode1
Tetrode2
Load2
Load1
Tetrode1
Tetrode2
Load2
Load1
Beam Pulse
Power
Time
30% overhead
3.5 ms
2.86 ms
Amplifier
Pulse
PLoad
PLoad
Normal beam operation
Amplifier testing
Courtesy:
Cooling task force,
Morten Jensen
But reliable, low maintenance loads were not
existing with minimum 50oC inlet and 80oC outlet !!!
ΔT ≈ 1oC
New Cooling Concept (22 Jan 2015)
ΔT ≈ 10oC
Outlet temp
Controlled to 60oC

## Slide 10
Resistive loads
Maximum power load
available today = 200 kWp
Maximum outlet temperature 90oC
d α Ip
L α Average power
d
Metallization
Indigenously
Developed
TEE combiner
For spokes:
400kWp
New resistor being developed
for ESS: 750 kWp @ 704 MHz
Technology Enhancement
d ≈ 8 inch, L ≈ 28 inch
L
Courtesy:
FREIA
Courtesy:
FREIA
Metallization: provides rf contact to the resistive coating

## Slide 11
Resistive loads
Cooling water
Inlet
Heat removal is efficient
Corrosive effects of high-purity DI water causes erosion of rf contacts. Thus resistor needs to be replaced.
To avoid fast erosion: The RF contacts are plated with Gold.
Needs maintenance !
In spite of Gold plating, after three years, resistor need to be replaced.
Cooling water
Outlet
-Increase in running cost of accelerator
-Increase in Man power requirement
Courtesy: Doug Horan (ANL)

## Slide 12
Now DI water no more interacts with metallization
Thus needs
zero maintenance !
Technology Enhancement
Heat removal is less efficient compared to earlier design
- Load becomes more compact as dielectric tube inside ceramic
Outlet

## Slide 13
Proposed design
For HB/MB load
New resistor
Development
Zero maintenance
New development for ESS

## Slide 14
Ferrite tiles glued with water cooled wall
Zero maintenance
RF and water circuit separate
Earlier Maximum return
temperature ≈ 40oC
Ferrite Load using ferrite tiles
Aluminum plate
Cooling channels
Hot surface
Adhesive
Ferrite
AFT changed gluing technology
- To take care of heat transfer to the cooling channels
- Adhesive withstands >> 80oC
- To tare care of different thermal expansions of ferrite and Al,
thermal stresses
Now outlet temperature = 80oC
Technology Enhancement

## Slide 15
Ferrite Energy Recovery Load
Development by MEGA, following merger of MCI into MEGA
(Basic R&D was carried in CERN by Fritz Casper for loads at high frequency)
New development for ESS
Max Outlet temperature 80o C
H-plane septa
Lossy ferrite powder used as absorber
# Lossy Ferrite in powder form is mixed with adhesive
# Applied on water cooled Septa
Eliminates risk of fracture due to thermal stresses
As ferrite molecular density is reduced, Watt /area reduces
Surface area increases, thus increasing avg. power handling capability
Staggering of
plates to self cancel
reflection

## Slide 16
1450 mm
Zero maintenance
RF and water circuit
separate
Proposed design for HB/MB load

## Slide 17
Technology Enhancement
Teflon cone
Water filled
cylindrical
column
Water Load
Length≈ 700 mm
DI water is used as absorbent
T=65oC
T=50oC
T=80oC
Return loss for load
50oC-80oC: S11 > 30 dB
E field < 0.8 MV/m
For input power 1500 MWp
Proposed design for HB/MB load

## Slide 18
ESS will be first one to use high temperature water cooled loads for Energy recovery.
The load designs are either NEW or with TECHNOLOGY ENHANCEMENT !
RF GROUP IS TAKING RISK
Thank you !

## Slide 20
Power to the load during Amplifier testing
Testing time < 600 hours / year
Increase in outlet temperature ≈ 10 oC
Power to the load during matched
Beam operation
6000 hours/year: When machine is running
Increase in outlet temperature < 1oC
Different Operating scenarios
Pdiss across load
Time
Beam Pulse
Pdiss
Time
30% overhead
3.5 ms
2.86 ms
Amplifier
Pulse
Power dissipated
in load