## Slide 2: ESS klystron modulator: tests at CERN
David Nisbet (CERN)
Sven Putz (CERN, now GSI)

## Slide 3: Introduction
Project outline
Design & construction
Results
Feedback
Conclusion

## Slide 4: Project Description
Modulator requirement identified for a high power 704MHz teststand at CERN
  Deliver 2.8MW electrical pulsed power to a klystron
  Flexible enough to adapt to several specifications, including ESS and SPL parameters
Modulator supplied by ESS through superconducting cavity collaboration
  Contract prepared and managed by ESS with some CERN input
  Selection of best offer which was based on simple LR bouncer topology
  Contract placed in 2011

## Slide 5: Modulator specifications
Parameter | SM18 / ESS | SPL | LINAC4 | 
Uk | -115 | -110 | -110 | kV
Ik | 25 | 25 | 50 | A
Ppulse | 2.88 | 2.6 | 5.5 | MW
Pavg | 161 |  | 20 | kW
PRR | 20 | 50 | 2 | Hz
Zk | 4.6 | 4.4 | 2.2 | kΩ
τpulse / τflat-top | 2.8 / 2.5 | 1.0 / 0.8 | 1.8 / 1.5 | ms
droop | 3 | 1 | 1 | %
droop compensation type | LR |  | LC | 
Design / Production | AMPEGON PPT GmbH |  | CERN / JEMA sa | 
Average Power | 161 | 138 | 20 | kW
Average power specification
Load

## Slide 6: Project execution
2012
2013
2014
2011
07 - call for tender
09 - TDR presentation
10 - dummy load revised TDR
03 - reception @25% (PPT)
05 - reception @100% (CERN)
09 - commissioning SM18
12 - contract start
10 - TDR approval (except dummy load)
10 - approval of dummy load TDR

## Slide 7: Electrical Schematic & Layout

## Slide 8: Modulator testing at CERN

## Slide 9: Resistive Dummy Load
air insulated
water cooled
Pavg 161 kW
11 m3 / 6 m2
2400
2300
2000
Load resistors and rating plate

## Slide 10: Uk measurements
3% of Uk
Droop meets specification (3% of nominal)
Rise time ~250us
Slow change of Uk during 24hr period of ~0.5%, to be compensated by RF Low Level
~250us
Operation at [115kV, 25A, 2.8ms]

## Slide 11: Uk measurements
Delivered system had very noisy signals leading to difficulties to validate performance
Diagnosis of HV measurement issues is not easy!
  Dedicated external voltage divider in oil with additional HV connections
Evolution of Uk measurement improvements

## Slide 12: AC Power Quality
Constant power operation was not a requirement
The non-balanced AC supply can be clearly seen
Should there be many systems on the same network, the problem will be more severe

## Slide 13: Project feedback
Overall the modulator is of a high quality design and construction
The supplier chose a sub-system design concept
  High dependence on sub-contractors
  Can be an issue when problems are encountered, due to lack of detailed expertise and issues of information flow
Contract / design
  Important that all employed technologies are understood by both contractor and client!
Load design and delivery
  Essential for contract execution; required design input from CERN to ensure an acceptable and successful solution

## Slide 14: Project feedback
Electronics implementation
  Takes a long time to implement and debug software
  PLC software is user friendly, however not yet stable or definitive
  Some design decisions on electronics execution could be better (grounding, noise)
  Difficult to correct some hardware problems if only discovered during reception
  Recommend a thorough specification that includes progressive testing program including interfacing in final software environment
Acoustic Noise
  75dB measured. Issue not to be ignored if there are many systems in a confined space
Water
  This is a reliability and availability driver. Recommend large margins between nominal and trip settings.
Transport
  Although clearly specified, not implemented correctly. Check maintenance procedures carefully.

## Slide 15: Status
Modulator is fully commissioned and operational on a LEP klystron in SM18
  Recently used for LINAC4 CCDTL cavity conditioning
Soon to be commissioned with a 704MHz klystron
Still some issues to be definitively resolved
  Software updates to be implemented and fully tested
  Definitive measurement hardware update to be implemented and fully tested

## Slide 16: Conclusion
Proven topology and design chosen to minimize contract risk
  In the end it was the details that mattered (controls, load, sub-contractors, …)
Highest average pulsed power system at CERN has been successfully commissioned
  Valuable contribution for long pulse experience
  Useful experience for subsequent strategy
Testing of long pulse high rep rate RF systems now possible
Many thanks to the ESS team for the support and perseverance to bring the system from concept to teststand reality

## Slide 17: Acknowledgements
ESS
  Carlos de Almeida Martins
  Karin Rathsman
  David McGinnis
CERN
  Sven Putz
  Julien Parra-Lopez
  Azmat Tanvir