## Slide 1: Status and Plans for the Target Safety System
Linda R. Coney
Group Leader – Target Safety and Controls
www.europeanspallationsource.se
April 1-2, 2015

## Slide 2: Outline
Intro
Hazard Analyses Update
Pilot TSS Design Development
Conclusions

## Slide 3: TSS – Purpose
TSS is a safety critical system designed to protect the public, workers, and environment from radioactive release
Active control and monitoring system
  It is likely that the TSS will need to be able to shut down the proton beam
  Actions not necessarily limited to beam shut down
Safety-credited system
  Essential to the licensing process for the ESS

## Slide 4: Target Controls & Safety Group – TSS Activities
Define requirements for the TSS
  Hazard analyses
  New ESS classification of safety functions & safety important components
  Review of SSM documentation
Design Pilot-TSS
  Complete system – logic, sensors, cable paths, PLCs, shutdown methods
  Defining interfaces for Pilot-TSS – CF , Accelerator, Target systems, ICS
Participate in safety activities at ESS
  Attend Safety Advisory Group meetings, safety classification from System Engineering, engage with SSM regarding safety controls

## Slide 5: Hazard Analyses – TSS Requirements Determination
Continuing Hazard Analyses on Target Station systems
  Review and update HA information for all systems
    include design changes & involve new personnel
  Connect systems g comprehensive analysis of chain of events
  Identify enveloping events for quantitative analysis
Qualitative Hazard Analysis
  Events evaluated for risk of radiologic release
  Design recommendations for Target Station systems
  Inputs and outputs for TSS
  TSS logic design
  Quantitative Hazard Analysis – dose rates & analyses
MPS risk analyses separate (within ICS Division responsibility)
  ICS collaboration with Zurich University of Applied Sciences (ZHAW)
  For machine protection only – not a safety system

## Slide 6: Hazard Analyses – Scope
Comprehensive analysis of all Target station systems
  Within Monolith (Target wheel, moderators, reflector, PBW) relevant primary cooling systems are included
Analysis of Active Cells Facility (remote handling, ventilation)
Active Cells Facility
Monolith
Wheel, Cold Moderator, Water Moderator,
Reflector, PBW, Instrumentation plugs
Utility rooms
Utility rooms
no access for operations
133 m
p+
Beam Dump

## Slide 7: Hazard Analysis – Procedure
System definition | Hazards List | Postulated Initiating events (PIE) | Top Event | Unmitigated Consequences, Time scale to destroy | Probability Occur & Severity | Unmitigated Risk Ranking | Protection/safety system equipment | Triggers | Probability Occur & Severity | Mitigated Risk Ranking | Design Recommend-ations List | Recommendations list for studies and investigations
Step 1:
What is the system?
System owner prepares a short definition. Presented at the first HA session.
Step 2:
What could happen?
What are the reasons?
Begun offline & discussed during a HA session.
Step 3:
What are the hazard scenarios? What are the consequnces?
Step 4:
Risk ranking. What is the probability? What is the severity?
Step 7:
Recommendation for design.
Request for studies for quantification of consequences.
HA session
HA session(s)
HA session(s)
(or more depending on progress)
Step 5:
How to detect? How to mitigate?
Step 6:
Risk ranking after mitigations.
Done offline by HA expert and system group. Discussed in next HA session(s).
Done offline by HA expert and system group. Discussed in next HA session.
HA session

## Slide 8: Hazard Analyses – Radiation Exposure Limits
FROM ESS GSO (General Safety Objectives) |  |  | FROM SSM
ESS Safety Objectives |  |  | 
Operating conditions Initiating event likelihood | Workers limit (effective dose) | Public limit (effective dose) | Public limit
Normal operation - H1 | 10 mSv/year | 0,05 mSv/year | 0,1 mSv 0,1 mSv 1 mSv
Incidents – H2 F > 10-2 Ex : loss of external power or target cooling | 20 mSv/event | 0,5 mSv/occurrence | 
Unexpected events - H3 10-4 < F < 10-2 | 50 mSv/event | 5 mSv/occurrence | 
Design Basis Accident – H4 10-6 < F < 10-4 | 50 mSv/event | 20 mSv/occurrence | 20 mSv
Highly improbable events – H5 10-7 < F < 10-6 Ex : plane crashes, major earthquake |  |  | 100 mSv
8
5
5

## Slide 9: Hazard Analyses – Status
Completed review of HA for:
  Water Moderator, Cold Moderator, Reflector
Ongoing
  Active Cells (Process Cells, Remote Handling)
  Ventilation systems (Active Cells, Utility Rooms, High Bay)
  Target system (Wheel & He cooling)
  Monolith (Proton Beam Window (PBW), Beam Dump)
    Bring in events initiated in other systems
    Moderators/Reflectors/Target wheel/Beam Events/Choppers
Next
  Active Liquid & Gaseous Storage
  Intermediate water systems
Move into Quantitative HA
  Start with Target wheel events – wheel stop & loss of He cooling
  Incorporate design recommendations & results from studies
  Identify significant events g refine TSS logic

## Slide 10: HA schedule
Initial analysis: Initial HA on Subsystem
HA review: HA Review, Internal and external PIE identified, Top Events identified, Qualitative risk assessment, SaF identified/proposed, Study recommendations identified
Quantitative Assessment: Studies are performed, Dose calculations, Quantitative risk ranking
April
May
June
March

## Slide 11: TSS Design & Development – Pilot TSS
Hazard analysis process is on-going & long term
Moving forward with the TSS design
  Make assumptions based on the information currently available from the HAs
  Incorporate appropriate redundancy & diversity
Assume TSS needs to:
  Detect stopped wheel rotation
  Detect loss of He cooling in wheel
  Shut down proton beam when these conditions are present
  Note: no quantitative results from Hazard Analysis yet. Possibility that requirements on TSS will change is understood.

## Slide 12: Pilot TSS – Implementation
Identify need for action by TSS for events from Hazard Analysis
Define safety functions (SaF)
  First attempt to implement ESS safety function categorization
  Define TSS portion of safety functions
  Evaluate severity – determine SaF classification & requirements for design
Design complete Pilot-TSS system to fulfil safety functions
  Logic design – requirements from classification, release limits, SSM
  Trigger mechanisms, sensors, PLCs, shutdown methods
  Interfaces – Accelerator, CF, Target Station systems, ICS
TSS Test Stand
  Prototype of TSS – safety PLCs, programming, implement design
  Automated test program for TSS logic

## Slide 13: Pilot TSS – Safety Function Classification
Apply ESS safety function classification scheme
  Note: Safety function severity is different from the mild/moderate/severe scale for the original event from which a safety function need was defined.
Ex. Consider a top event from the Hazard Analysis that is H3 with an dose of 3 mSv to the public
  This is above the allowed limit – Risk Ranking of “Severe” and requires mitigation by a safety function
  Identify safety function Severity Scale from table: 3 mSv = Medium severity g SaF C2
  C2 requires: redundancy, independence of redundant train, physical separation, qualification to environment, verification
  Does not require diversity
Severity Scale | Criteria
High | Radiological consequences for the public > 20 mSv (H4) Radiological consequences for workers > 50 mSv (H4)
Medium | Radiological consequences for the public > 1 mSv (H3) Radiological consequences for workers > 20 mSv (H2)
Low | Radiological consequences for the public > 0.1 mSv (H2) Radiological consequences for workers > 10 mSv
ESS-0016468

## Slide 14: Pilot TSS – Design Concepts
Monitor target systems
    Target cooling system – He flow, He temperature or pressure
    Target wheel – shaft speed, drive load, wheel motion (monitoring plug?)
    Defining optimal detection methods & interfaces with system owners
  Two shutdown mechanisms to stop beam
    Ion source and possibly RFQ
    Direct access/priority to shutdown mechanisms
    Defining interfaces with accelerator and MPS/PSS
  Use safety-rated PLCs
  Two separate TSS rooms in Target building –
    Identified in CF plan
  Independent paths to each beam shut-off system
    Defining cable paths with CF
  Separate from ICS controls – cable-trays, UPS, shutdown mechanisms
  Satisfy requirements & protect public with as-simple-as-possible system

## Slide 15: Pilot TSS – Logic
Read
Target wheel cooling
He temp
Target wheel cooling
He flow
Target wheel motion
< TBD deg C
> TBD g/s
> TBD rpm
All conditions
satisfied
Evaluate
Act
Allow proton beam

## Slide 16: Pilot TSS – Draft Overall Layout
2oo3
1oo2

## Slide 17: Plan for TSS Development
Qualitative Hazard Analyses Q1-Q2 2015
Quantitative Hazard Analyses Q1 2015 – Q1 2016
Description of Pilot TSS – logic & interfaces Q1 - Q4 2015
  MS: PDR of TSS (Pilot) November 2015
Test Stand 2015 – 2016
Design of TSS Architecture
  Includes documentation, finalization of interfaces, & safety analysis of system architecture
  MS: CDR of TSS System Summer 2016
Manufacturing 2017
  Supplier chosen Mar 2017
  Delivery to site Feb 2018
Installation/Testing Feb 2018 g Jan 2019

## Slide 18: TSS – Conclusions
Hazard Analyses process moved into high gear
  New resources in place
  Qualitative analysis scheduled to finish by June
  Next:
    Quantitative analyses to clarify TSS and target system requirements
    Connect HA results with safety function classification
Moving forward with Pilot-TSS design
  Enables progress without requiring completion of Hazard Analyses
  Define: requirements, interfaces, details
  Next: understand safety function classification implications for TSS design
  Aim for PDR late 2015
TSS group directly involved in safety activities at ESS
  Participate in Safety Advisory Group meetings, safety classification from System Engineering, engaged with SSM on safety controls

## Slide 20: TSS Context – ESS Control Systems
TSS - Limit transfer of radioactive contamination to the public, workers, and environment
PSS - Suppress radiologic hazards by switching off the proton beam
  Control access to restricted areas during operations
MPS – Protect investment from damage due to beam losses and malfunctioning equipment
  Optimize integrated machine performance
  Stop beam – Beam Interlock System
TSS – Independent safety-qualified system
g Not tied into other ICS systems
Personnel Safety System

## Slide 21: Hazard Analyses – Target Station Components
Systems evaluated during Hazard Analyses – including relevant primary fluid systems
  Cold Moderator
  Water Moderator
  Reflector
  Monolith
  PBW
  Target (wheel, drive, He cooling system)
Ventilation, Intermediate cooling systems, Remote Handling, Beam Dump
Instrumentation
  proton beam and target monitoring
Proton beam
10 m
11 m

## Slide 22: Hazard Analyses – Risk Ranking
Severity Probability | Minor | Moderate | Severe | Dose Limit
H1 (Normal Operation) | Tolerable | Risk reduction recommended | Unacceptable | 0.1 mSv/year 10 mSv/year
H2 (Incidents) | Tolerable | Risk reduction recommended | Unacceptable | 0. 1 mSv/event 20 mSv/event
H3 (Unexpected events) | Tolerable | Risk reduction recommended | Unacceptable | 1 mSv/event 50 mSv/event
H4 (Design basis Accident) | Tolerable | Risk reduction recommended | Unacceptable | 20 mSv/event 50 mSv/event
 | < 10% of limit | 10 % to 100% of limit | > limit | 
 | Actual numbers depend on the probability category of the event – H1 through H4 |  |  | 
Categories for probability & consequences

## Slide 23: Pilot TSS – Interfaces with ICS systems
TSS signal to Target MPS verifying that it is functional
TSS may send data into EPICS via ICS control box
  Interface under evaluation
Independent sensors, actuators, cables, cable trays, etc.
  Ex. MPS and TSS both capable of beam shut off at ion source

## Slide 24: Pilot TSS – CF Interfaces
TSS Rooms in Target Building (D02 & D04)
Cable paths – sensors to rooms, rooms to accelerator front end
24