## Slide 1: Classification Primary Water Systems Sorting Equipment to Ensure Adequate Quality for Radiologic Safety
Per Nilsson
Håkan Carlsson
www.europeanspallationsource.se
Apr 01, 2015

## Slide 2: Classification
Sys X
Sys Y
Sys Z
Class A
Class B
Class C
Req 1
Req 2
…
Req 1
Req 2
…
Req 1
Req 2
…
System/Component
Classes
Requirements
Action 1
Action 2
…
Action 1
Action 2
…
Action 1
Action 2
…
Actions;
We have to …
Classification
Process
References to standards
Criteria
Iterations

## Slide 3: Safety Classification / Quality Classification
SSMFS 2008:17
This explains the sub-classification: Quality Class
SSM 133285 Special conditions for ESS
This is the requirement for Mechanical Quality Class
Notes: SSMFS 2008:17 - Application from ESS to SSM

## Slide 4: ESS Safety Functions - ESS-0016468

## Slide 5: ESS Severity Scale & Event Classification

## Slide 6: Function categorization example
Events relating to e.g. Reflector Water Cooling
Event 1
Event 2
Event 3
Event N
SaF C2
Safety function Category
This is a category of a function, not the system!
ESS-0016468 Classification Guide

## Slide 7: Deriving (nuclear safety) requirements for classes
Systems/ Components
Safety Function
Actions: (QA, Procedures) Analysis
Materials Manufacturing Installation
Inspection Testing
etc
Risks - Events
Safety
Class
Quality
Class
Code
Class
Design/define the systems and context
Define (enveloping) events and frequency (H1-H5)
Determine and categorize safety functions to prevent events (SaF)
Event Consequences
Calculate dose consequences of events (H1-H5)
Determine safety classification of equipment (SIC)
Determine quality classification of equipment in disciplines, e.g. mechanical
Choose classification in the codes and standards within the disciplines

## Slide 8: Classification: Deriving (nuclear safety) requirements for each system
Systems/ Components
Safety Function
Actions: (QA, Procedures) Analysis
Materials Manufacturing Installation
Inspection Testing
etc
Risks - Events
Safety
Class
Quality
Class
Code
Class
Design/define the systems and context
Define (enveloping) events and frequency (H1-H5 probab.)
Determine and categorize safety functions to prevent events (SaF)
Event Consequences
Calculate dose consequences of events (H1-H5 criteria)
Determine safety classification of equipment (SIC)
Determine quality classification of equipment in disciplines, e.g. mechanical
Choose classification in the codes and standards within the disciplines
PBS
Modes
HAZOP
Rules for SaF & SIC
SSM Conditions
Codes, e.g. RCC-MRx
GSO
Release Factors
Conversion Factors
Inventories
We have the green
Blue are in work

## Slide 9: From Events to Code Classes
> H4
> H3 public > H2 workers
> H1
SaF C1
SaF C2
SaF C3
SIC 1
SIC 2
SIC 3
Severity of Event (at failure of function)
Safety Function (for system to fulfill)
Safety Class (of system or part)
N1MR
N2MR
N3MR
Code Class (requirements on part)
This figure is simplified! There are other additional criteria, requirements and options
1
2
3
Quality Class (of part in discipline)
Preventing loss of integrity
Notes: Explain Criteria, Requirements, Options

## Slide 10: From Events to RCC-MRx Code Classes
> H4
> H3 public > H2 workers
> H1
SaF C1
SaF C2
SaF C3
SIC 1
SIC 2
SIC 3
Severity of Event (at failure of function)
Safety Function (for system to fulfill)
Safety Class (of system or part)
N2MR
N3MR
RCC-MRx
Code Class
This figure is simplified! There are other additional criteria, requirements and options
1
2
3
Mechanical
Quality Class
Preventing loss of integrity
Notes: Diversifying, Redundancy ….?

## Slide 11: From Events to Ventilation Quality Class
> H4
> H3 public > H2 workers
> H1
SaF C1
SaF C2
SaF C3
SIC 1
SIC 2
SIC 3
Severity of Event (at failure of function)
Safety Function (for system to fulfill)
Safety Class (of system or part)
Code?
VSQ
VNQ
Ventilation
Safety Quality
Code?

## Slide 12: Deriving (nuclear safety) requirements for classes
Plant Breakdown Structure (PBS) and Modes exist
HAZOP exist (for moderators and reflectors, shielding is planned, purification will be)
→ Events can soon be postulated
Release Factors and Inventories in water are only estimated
Conversion Factors exist
→ Consequences can soon be calculated

## Slide 13: Deriving (nuclear safety) requirements for classes
SaFs and SICs cannot be stringently derived without events and consequences.
→ The SICs do however depend strongly on the severity of the events.
That can be estimated before the derivation.
It means taking a risk to make a wrong classification!

## Slide 14: Deriving (nuclear safety) requirements for classes
RCC-MRx chosen for safety components Choosing code class (in RCC-MRx) gives range of requirements, e.g. QA, in European framework
RCC-MRx does not guide, but points up to a French order for reactors and European directives for pressure equipment.
The French order points explicitly to some specific parts of reactors, but also contains some qualitative and actually one quantitative criterion!

## Slide 15: Conclusion: Code Class for Primary Water Systems
Class not decided yet
RCC-MRx:
  Many procedures and documents are the same as PED (Pressure Equipment Directive, Swedish Law)
→ No waste (yet) in applying RCC-MRx N3MR
Notes: Bra hjälp med dokumentation, analyser etc, men QC-krav kan bli omfattande ! AK styrs mest av SSM krav !!

## Slide 16: RCC-MRx General Documents
Section I General RCC-MRx: RDG 3000 Documents to be Prepared
RDG 3100 Equipment Specification
RDG 3200 General Technical Documents RDG 3210 Comprehensive Layout and Referencing Documents
RDG 3220 Components Part List
RDG 3230 Description of Fabrication Shops
RDG 3300 Non-Conformance Report and Deviation Report
RDG 3310 Non-Conformance Report
RDG 3320 Deviation Report
RDG 3400 Technical Preparation, Follow-Up and Final Report Documents
RDG 3410 Follow-Up Documents
RDG 3420 Certificate of Compliance
RDG 3430 End-of-Design and Manufacturing Report
General Section III:
RA 3000 Documents to be Prepared in application of Section III
RA 3100 Equipment Specification
RA 3200 General Technical Documents RA 3210 Comprehensive Layout and Referencing Documents
RA 3220 Components Part List
RA 3230 Description of Fabrication Shops
RA 3300 Documents Relating to the Design
RA 3310 Design and Calculation Reports – Design Report
RA 3400 Documents Relating to Procurement
RA 3410 Technical Part and Product Manufacturing Programme
RA 3420 Part or Product Sub-Purchase
RA 3430 Part or Product Procurement Test Report
RA 3500 Documents Relating to Fabrication Processes (other than welding)
RA 3510 Fabrication Procedures or Instructions
RA 3600 Welding Documents
RA 3610 Welding Data Package
RA 3620 Filler Materials Acceptance Documents and Welding Procedure Documents
RA 3630 Welding Reports
RA 3700 Documents Relating to Examinations and Tests
RA 3710 Examination and Test Procedures or Instructions
RA 3720 Examination and Test Reports
RA 3730 Hydrostatic Test Reports
RA 3800 Non-Conformance Report and Deviation Report
RA 3900 Technical Preparation, Follow-Up and Final Report Documents
RA 3910 Follow-Up Documents
RA 3920 Certificate of Compliance
RA 3930 End-of-Manufacturing Report

## Slide 17: Water moderator system

## Slide 18: Risk Analysis

## Slide 19: Events with unmitigated consequences
Event
T1.4.1 circuit rupture inside the monolith
T1.4.2 circuit rupture inside the connection and utility rooms
T1.2.5 leak into/from the intermediate cooling loop
T1.2.5 leak into radioactive effluent circuit and into N2 supply
T2.2 stoichiometric combustion of (H2/D2)-O2
T2.3. temperature decrease

## Slide 20: Events with unmitigated consequences
Event
T1.4.1 circuit rupture inside the monolith
T1.4.2 circuit rupture inside the connection and utility rooms
‘T1.2.5 leak into/from the intermediate cooling loop
T1.2.5 leak into radioactive effluent circuit and into N2 supply
T2.2 stoichiometric combustion of (H2/D2)-O2
T2.3. temperature decrease
Chain of events:
Complete break before heat exchanger
Water (~30C) runs out from GLS-tank and Delay-tank (~1m3)
Most runs to floor drains
Smaller fraction (adiabatic saturation in air ~4g/m3) is ventilated
The room is ventilated (300m3/h -> 1.2 kg/h) for one hour -> 1.2 kg

## Slide 21: Release for that specific event
Inventory 5 GBq 3H / kg (SNS & SINQ ~1 GBq / kg)
Release 1.2 kg -> 6 GBq
ESS-0003690 (unplanned) / 3H :
0.44mSv/3.2PBq * 6 GBq = 0.8 nSv
< 0.1 mSv -> No SaF!
Have to check other events and worker impact too!

## Slide 22: t-TAC Committee
“Are the proposed safety classification and TSS approaches sensible and likely to define a path towards safe operation of the ESS Target Station?”