## Slide 2: SIL Assessment for ESS PSS SIFs
ESS PSS PDR
PRESENTED BY Fan YE and DENIS PAULIC

## Slide 3: Agenda
1 Introduction to PSS SIL Assessment
2 Accelerator PSS Safety Instrumented Functions (SIFs)
3 Accelerator PSS SIL Assessment
4 Target Station PSS, Bunker PSS, DREAM PSS SIFs
5 Target Station PSS, Bunker PSS, DREAM PSS SIL assessment

## Slide 4
TS PSS, Bunker PSS, DREAM PSS SIFs
4

## Slide 5: TS PSS SIFs
TSPSS_SIF1
If any ESOB in Target PSS controlled area is detected pressed when bending magnets are energized (BoT allowed), de-energise the Proton Beam Actuators.
TSPSS_SIF3
If there is access to Target PSS controlled area (any access door or emergency exit door detected open) and bending magnets are detected energized (BoT allowed), de-energise the Proton Beam Actuators.
Access doors level 91 (2 doors, 2 switches per door)
Sliding concrete door level 103 (1 door, 2 switches)
Sliding concrete door level 115 (1 door, 2 switches)
Double-gated access door level 115 (2 leafs per door, 2 switches per leaf - 8 switches in total)
Emergency exit door level 90 (1 door, 2 switches)
Emergency exit door level 103 (1 door, 2 switches)
Feedback signals, bending magnet contactors (4 contactors’ feedback signals in total)
PSS NCL PLC
TS PSS PLC
Nexus PLC
2 contactors for ISrc HVPS
Grounding relay + contactor relay

## Slide 6: TS PSS SIFs
TSPSS_SIF4
TSPSS_SIF4_1
Upon removal of the entry key to access door DIS602 from the door lock unit, lock the door DIS602 via solenoid.
TSPSS_SIF4_2
Upon removal of the entry key to access door DIS605 from the door lock unit, lock the door DIS605 via solenoid.
TSPSS_SIF4_3
Upon removal of the entry key to sliding concrete door to D02.103.4003 from the door lock unit, lock the sliding concrete door to D02.103.4003 via solenoid.
TSPSS_SIF4_4
Upon removal of the entry key to sliding concrete door to D02.115.4003 from the door lock unit, lock the sliding concrete door to D02.115.4003 via solenoid.
TSPSS_SIF4_5
Upon removal of the entry key to access door to D02.115.4001 (Connection Cell) from the door lock unit, lock the access door to D02.115.4001 (Connection Cell) via solenoid.
This is done without a logic solver. PLC will monitor the safety circuits from the lock unit to ensure the door is locked.

## Slide 7: TS PSS SIFs / Bunker PSS SIFs
BunPSS_SIF8_1
If any of the LSS in D01 is detected open, lock the South Bunker Access key (SBAK) in position ON in slot 5 of Unit 1.
BunPSS_SIF8_2
If any of the LSS in D03 is detected open, lock the North Bunker Access key (NBAK) in position ON in slot 4 of Unit 1.
These functions prevent people from being exposed to gamma radiation in Target basement area and Bunker PSS controlled area.
TSPSS_SIF6
If the Target Access key is detected out of position ON in Slot 3 of the key exchange unit 1, de-energise the following EUC:
  Light Shutter Systems (LSS) Actuators in D01.
  Light Shutter Systems (LSS) Actuators in D03.
BunPSS_SIF6_1
If the South Bunker Access key (SBAK) is detected removed from position ON in Slot 5 de-energize the following EUC:
  Light Shutter Systems (LSS) Actuators in D01
BunPSS_SIF6_2
If the North Bunker Access key (NBAK) is detected removed from position ON in Slot 4 de-energize the following EUC:
  Light Shutter Systems (LSS) Actuators in D03

## Slide 8: Bunker PSS SIFs
If any safety token is detected removed from units 2 in North and South Bunkers and bending magnets are detected energized (BoT allowed), de-energise the following EUC:
  Proton Beam Actuators
  Light Shutter Systems (LSS) Actuators in D01.
  Light Shutter Systems (LSS) Actuators in D03.
BunPSS_SIF7
Safety circuits from Bunker South key exchange unit 2 (2 safety circuits per unit)
Safety circuits from Bunker North key exchange unit 2 (2 safety circuits per unit)
Feedback signals, bending magnet contactors (4 contactors’ feedback signals in total)
Bunker North PSS PLC
Bunker South PSS PLC
Nexus PSS PLC
PSS NCL PLC
2 contactors for ISrc HVPS
Grounding relay + contactor relay
2 contactors for each LSS (16 in total)

## Slide 9: DREAM PSS SIFs
DREAMPSS_SIF1
  If any ESOB in the DREAM PSS controlled area is pressed, de-energise the instrument shutter.
    Additionally, if the instrument shutter is detected open after the ESOB is detected pressed, and the bending magnets are detected energized (BoT allowed), de-energise the Proton Beam Actuators.
DREAMPSS_SIF3
If the access door to DREAM PSS controlled area is detected open, de-energise the instrument shutter.
    Additionally, if the instrument shutter is detected open 5 seconds after the door is detected open, and the bending magnets are detected energized (BoT allowed), de-energise the Proton Beam Actuators.
Proton beam interlock if BoT allowed
6 ESOBs
Feedback signals, bending magnet contactors (4 contactors’ feedback signals in total)
2 safety switches on the instrument shutter
DREAM PSS PLC
Nexus PSS PLC
PSS NCL PLC
Solenoid valve (PSS owned)
Pneumatic actuator for instrument shutter
2 contactors for ISrc HVPS
Grounding relay + contactor relay
2 contactors for each LSS (16 in total)

## Slide 10: DREAM PSS SIFs
DREAMPSS_SIF2
      If the DREAM main key is detected out of position ON, de-energise the instrument shutter.
  DREAMPSS_SIF6
      If the DREAM instrument shutter is detected open, lock the DREAM main key in position ON.
DREAMPSS_SIF4
      If the entry key to open the access door to DREAM cave 1 is detected removed from position ON in the lock unit, de-energise the solenoid on the door's lock unit.
DREAMPSS_SIF5
      If the radiation monitor downstream the DREAM instrument shutter shows high radiation or has an error when the shutter is closed and DREAM access key to cave 1 is out of position ON, de-energise the Proton Beam Actuators.

## Slide 11
TS PSS, Bunker PSS, DREAM PSS SIL Assessment
5

## Slide 12: SIL verification Results
Low Demand SIFs
SIF Tag | Selected PFD Target | PFD Achieved | Selected SIL Target | Max Allowable SIL (Architectural Constraints) | Result
TSPSS_SIF1 – ESOB interlock from Target area | N/A | 4.6E-4 | SIL 1 | SIL 2 | Passed
DREAMPSS_SIF1 - ESOB interlock from DREAM PSS | N/A | 3.7E-2 | SIL 1 | SIL 1 | Passed
DREAMPSS_SIF5 - High radiation interlock in DREAM | 1.0E-2 | 4.2E-4 | SIL 1 | SIL 2 | Passed

## Slide 13: SIL verification Results
High Demand
SIF Tag | Selected PFH Target | PFH Achieved (/hr) | Selected SIL Target | Max Allowable SIL (Architectural Constraints) | Result
TSPSS_SIF3 - Target Access Door Interlock | 1.1E-6 | 2.2E-8 | SIL 1 | SIL 3 | Passed
TSPSS_SIF4_1 – Target level 91 (Basement) access door DIS602 lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
TSPSS_SIF4_2 – Target level 91 (Basement) access door DIS605 lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
TSPSS_SIF4_3 – Target level 103 sliding concrete door lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
TSPSS_SIF4_4– Target level 115 sliding concrete door lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
TSPSS_SIF4_5– Target level 115 access door lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
TSPSS_SIF6 – Target access key LSS interlock | [HOLD] | 9.7E-8 | [HOLD] | SIL 2 | [HOLD]
BunPSS_SIF6_1– Bunker access key LSS interlock in Bunker South (D01) | [HOLD] | 4.3E-8 | [HOLD] | SIL 2 | [HOLD]
BunPSS_SIF6_2– Bunker access key LSS interlock in Bunker North (D03) | [HOLD] | 6.7E-8 | [HOLD] | SIL 2 | [HOLD]
BunPSS_SIF7– Safety tokens interlock | [HOLD] | 1.0E-7 | [HOLD] | SIL 3 | [HOLD]
BunPSS_SIF8_1– SBAK lock | [HOLD] | 9.6E-8 | [HOLD] | SIL 2 | [HOLD]
BunPSS_SIF8_2– NBAK lock | [HOLD] | 9.9E-8 | [HOLD] | SIL 2 | [HOLD]
DREAMPSS_SIF2– DREAM main key interlock | 2.3E-7 | 3.1E-6 | SIL 2 | SIL 1 | Failed
DREAMPSS_SIF3– Access door interlock in DREAM PSS | 1.1E-6 | 3.1E-6 | SIL 1 | SIL 1 | Failed
DREAMPSS_SIF4– DREAM cave access door lock | 1.1E-6 | 1.1E-7 | SIL 1 | SIL 2 | Passed
DREAMPSS_SIF6– DREAM main key lock | [HOLD] | 9.4E-8 | [HOLD] | SIL 2 | [HOLD]

## Slide 14: Event Tree Analysis (ETA)
Similar to ACC PSS ETAs:
ETA01 – Inadvertent beam operation whilst person in hazardous area, Electric shock hazard
ETA02a – Inadvertent beam operation whilst person in hazardous area (access without key), Radiation hazard
ETA02b – Inadvertent beam operation whilst person in hazardous area (access with key), Radiation hazard
ETA06 – Radiation risk due to off-normal beam
ETA03 – Inadvertent opening of Instrument Shutter whilst person in hazardous area: motion control failure

## Slide 15: Event Tree Analysis (ETA)
ETA04 – Intrusion through access door: override key used for access

## Slide 16: Event Tree Analysis (ETA)
ETA05 – Inadvertent opening of Instrument Shutter whilst person in hazardous area: people left in area, Radiation hazard

## Slide 17: Questions to the Committee
TS PSS, Bunker PSS, DREAM PSS
Is the approach for the initiating event where a person is missed by search and operation initiated acceptable?
Are the presented set of identified Safety Instrumented Functions (SIFs) properly formulated, and do they fulfil the overall safety functions derived from the DREAM RA?
Do you have any recommendation/example for reliability data used for equipment similar to the DREAM instrument shutter?

## Slide 18: Thank you for your attention!

## Slide 19: Backup slides

## Slide 20: ACCPSS_SIF3_2
Access door interlock – E-Exit1
Zone 1
NCL
Zone 2
NCL
Zone 3
SPK
Zone 4
MBL
Zone 5
HBL1
Zone 6
HBL2
Zone 7
HEBT
Zone 8
A2T
Run slideshow on this slide
E-Exit 1

## Slide 21: ACCPSS_SIF3_3
Access door interlock – E-Exit2
Zone 1
NCL
Zone 2
NCL
Zone 3
SPK
Zone 4
MBL
Zone 5
HBL1
Zone 6
HBL2
Zone 7
HEBT
Zone 8
A2T
Run slideshow on this slide
E-Exit 2

## Slide 22: ACCPSS_SIF3_4
Access door interlock – HEBT90
Zone 1
NCL
Zone 2
NCL
Zone 3
SPK
Zone 4
MBL
Zone 5
HBL1
Zone 6
HBL2
Zone 7
HEBT
Zone 8
A2T
Run slideshow on this slide
HEBT PAS

## Slide 23: ACCPSS_SIF3_5
Access door interlock – E-Exit 3
Zone 1
NCL
Zone 2
NCL
Zone 3
SPK
Zone 4
MBL
Zone 5
HBL1
Zone 6
HBL2
Zone 7
HEBT
Zone 8
A2T
Run slideshow on this slide
E-Exit 3

## Slide 24: ACCPSS_SIF3_6
Access door interlock – E-Exit 4 & A2T E-Exit
Zone 1
NCL
Zone 2
NCL
Zone 3
SPK
Zone 4
MBL
Zone 5
HBL1
Zone 6
HBL2
Zone 7
HEBT
Zone 8
A2T
Run slideshow on this slide
E-Exit 4
A2T E-Exit