## Slide 1: Integrated Control System IT Infrastructure decisions, issues & progress TAC 12
Remy Mudingay
ESS/ICS
Date: 2015-10-15

## Slide 2: Content
Scope of the Control System Infrastructure
Issues with the Temporary & Main Control room
Overview, decisions, issues & progress of the :
  Control System Data Centre
  Control System Network
Examples :
  Neutron Instrument and the Control System Network
  Strategy for the Accelerator installation
Lab Setup

## Slide 3: Scope: Infrastructure WP 14.7
The scope of this work package is to design, develop and procure the IT infrastructure required for the Control System to operate.
It has the following work units:
Control Room 14.7.1
  Design and implementation of the centralized ESS Control Room, which allows the Accelerator, Target, Neutron Instruments and Conventional Facilities to be controlled from the same room.
Data Centre 14.7.2
  Provide servers and file storage infrastructure required for normal operation during development, commissioning and operations phase.
Cabling & Wiring 14.7.4
  Covers the efforts and material required for connecting devices to the ICS through to the IO Controllers.
Control System Networks 14.7.3
  Design and implementation of the networks between IO Controllers, Control Room(s) and Data Centre.
Notes:   Is the scope for the infrastructure work package appropriate and precise enough?

## Slide 4: Issues with the Main Control Room(MCR) and Temporary Control Room (TCR)
MCR
  Available Q2 2019
    Target commissioning June 2019
  Secondary ICS server room & network room
    Redundancy
TCR
  Available Q2 2017
    Accelerator commissioning Q3 2017
  Requirements gathering process has begun
    Initial requirements from Beam Physicists
  Issues with PSS
    What should go in the TCR?
      3-5 dedicated PSS racks
      Issue – move to the MCR and re-commission, re-validate PSS (lots of effort)
    Instead of using the TCR – PSS’ preferred option is a 10m x 10m area in Klystron gallery
Notes: Need to go through this again.

## Slide 5: Control System Data Centre & Network
Capacity
  Modular
  Scalable
Openness
  Open standards
  Open Source
Robust
  High availability
Secure
  Authentication
  System Monitoring
Integration
  Simple
  Logical
Models (Data Centre & Network)
  Proven & Innovative technologies
  Trends
    Fulfill current & future needs
Service
  High level of service
  Anticipate needs
2x 10Gb/s
2x 40Gb/s
Access
Core
Data Centre

## Slide 6: Network & Computing (data centre)
General purpose Network
(GPN)
Neutron Instrument Network (NIN)
Technical Network (TN)
Stakeholders
DMSC
ICS
IT
Data acquisition
Data analysis
Office & labs
Internet access
EPICS control network
Timing system
?
?
?
Internet

## Slide 7: Network & Computing working groups
NSS, DMSC, ICS & IT
  Progress
    Shared infrastructure (DMSC & ICS)
      Communications room (Experimental halls & Instrument stations & control room)
      Fibre routes
    Standards
    IP addressing scheme
    Cabling & Labelling
  To do
    Security policies
    Scope of work
      Responsibilities
    Connectivity
    Computing working group meeting
ESS Electronics Hardware Harmonization Committee (E2H2C)
Computing, signal processing, networking, fieldbuses Working Group
Computing
Networking

## Slide 8: Control System Network fibre termination (decision)
Klystron gallery
Cryo
building
Central utility
Server hall
Target building
Beam lines
Control room
Substation
Substation
Dedicated COMMS room
Shared (NSS/IT)
Closed Cabinet
Open Rack

## Slide 9: Communications room (COMMS room) Recommendations sent to CF (decision)
height 47U or 2200mm, nominal width of 600mm, maximum depth of 800mm
2 fiber enclosures and 3 copper patch panels, cable management accessories and network communication equipment. Access control
Max cabling distance 90m between the COMMs room and the Equipment Outlet (EO).
ISO/IEC 11801 for generic cabling for telecommunications for twisted pair copper interconnects.

## Slide 10: Distances – COMMS room to core network (decision)
Chart: 
| > 500m (87,5%) | < 500m (12.5%)
Fibre routes | 21 | 3
Termination point | Distance metres
GO2 to HO1 Route A | 700
GO4 to HO1 Route A | 240
GO4 to GO2 Route A | 240
HO5 to HO1 Route A | 2400
HO6 to HO1 Route A | 80
FO3 to HO1 Route A | 750
B01 to HO1 Route A | 1500
DO2 to HO1 Route A | 1000
DO4 to HO1 Route A | 1000
DO7 to HO1 Route A | 1000
DO8 to HO1 Route A | 1000
EO4 to HO1 Route A | 1000
GO2 to HO1 Route B | 2500
GO4 to HO1 Route B | 3000
GO4 to GO2 Route B | 800
HO5 to HO1 Route B | 800
HO6 to HO1 Route B | 3100
FO3 to HO1 Route B | 2500
B01 to HO1 Route B | 3000
DO2 to HO1 Route B | 2500
DO4 to HO1 Route B | 2000
DO7 to HO1 Route B | 2000
DO8 to HO1 Route B | 2000
EO4 to HO1 Route B | 1000
Single mode fibre(SMF) / Multi mode fibre(MMF)

## Slide 11: Global fibre route, COMMS rooms & Core Network (decisions & uncertainties)
Klystron gallery
Cryo
building
Central utility
Server hall
Target building
Beam lines
Control room
Substation
Substation
2017
2019
Global route
Manhole every 50 - 120m
Microducts
Notes: Review

## Slide 12: Conceptual design of the Control System Network topology - option A (2nd SH in MCR)
Accelerator Building - G02
Target Building - D02
Experimental zones - D and E buildings (excluding D02)
H05
H06
Cryo Plant
Main Control Room (MCR)
Access switch
Fibre 10GbE to SH
Core switch
Building
Server Hall (SH)
x2
x8
x1
x4
x26
x1
x1
x2
x1
x26
x4
Fibre 40GbE
Fibre 10GbE to MCR
x4
x1
x2
x1
x26
x1

## Slide 13: Conceptual design of the Control System Network topology - Option B (single SH)
Accelerator Building - G02
Target Building - D02
Experimental zones - D and E buildings (excluding D02)
H05
H06
Cryo Plant
Control Room - B01
Access switch
Fibre 10GbE to SH
Core switch
Building
Server Hall (SH)
x2
X4
x2
x8
x2
x52
x2
x2
x2
x2
x26
x4

## Slide 14: Conceptual Control System Network Architecture
Diagnostics
Network (DN)
Isolated
Scope?
EPICS V3/4 gateway
wireless
Virtual
VPN/SSH gateway
Web services
Server farm
Storage
Firewall/Router
GPN|NIN
Motion controllers
PLC
TN
IO Controller
IO Controller
IO Controller
Proposed solution
Implications
Explore use cases
Security
  Vulnerability assessment
Explore alternatives
Other
Notes: Motion controllers
Other devices
Single network port, which network would they go into?
How would you both address the

## Slide 15: Neutron Instrument & Control System Network
Timing system
Technical Network
Neutron Instrument Network
Instrument control
workstation
IO Controller
Dedicated network switch
EPICS V3/4 gateway
  Read access for all
  Write access only on local instrument workstation
General Purpose Network
EPICS Gateway
EPICS Gateway

## Slide 16: Klystron gallery CS Network installation strategy
Piecemeal installation
  Modular cassettes (pre-terminated)
    Copper
      IO Controllers
      Other devices
    Fibre
      Timing
      Network switch
  Network switch per rack row
  Labelling standard TBD
    Internal handbook based on ANSI/TIA 606-A
    Naming convention

## Slide 17: Klystron gallery: IO Controller – Core Network
Equipment Rack
x ?
Termination point
Core network
Termination point
1GbE Cu
ISO 11801 Cat 6A
Fibre trunk Counter- clockwise
Fibre trunk clockwise
1/10GbE f/o
IO Controller
Network Switch L2
Single logical network multi-layered switch
8P8C/RJ45 modular
patch panel
Fibre optic termination
Patch panel
Fibre optic termination Patch panel
40GbE f/o
Rack row
Core network

## Slide 18: Exploring maintenance use cases for Klystron gallery & Accelerator tunnel
Wireless network
  Available only during shutdown & maintenance
    iPDU (intelligent power supply unit)
  Security
    Radius 802.1X
      AAA
        PEAP
        LDAP (group + attributes)
    Dynamic VLAN assignment
      Based LDAP profile (groups/attributes)
    Process Variable/Channel Access gateway

## Slide 19: Lab infrastructure
Virtualisation
  KVM(Kernel virtual machine hypervisor)
    Images
    staging
NFS central storage
  ZFS
    Mirror (8x 1TB + 4 hot spare disks)
    Snapshots
    Compression
    Quotas
    File-level checksum
    Backup
    Benchmarks
      1.6GB/s local async & 900MB/s local sync
      400MB/s NFS async* & 381MB/s NFS sync*
Archiver appliance testing
  Performance
    Per thread disk IO requirements
    Configuration
      Number of Archivers
      Storage types
    File-system
    Bench
EEE
(ESS EPICS Environment)
DNS
CSentry
VM
images
Application
Data
NFS
CCDB
IOC factory
Boot server
tftp
DHCP
Network attached Storage
Virtualisation
ArchiverA
Archiver
B
Distributed
Storage
* Network limitation
Done
Current
To do

## Slide 20: Control System Infrastructure
Thank you