## Slide 1: Preliminary Design of Safety Credited Active Controls
Mikael Olsson
Control engineer – Target control
www.europeanspallationsource.se
15-10-15

## Slide 2: Agenda
Purpose
Pilot TSS: events
Pilot TSS: system inputs and output
Pilot TSS: functions
Pilot TSS: architecture
Planned next steps

## Slide 3: Purpose of Target Safety System (TSS)
TSS is the ESS safety credited active monitoring and control system that shall:
  ”…protecting workers and the public from exposure to unsafe levels of radiation, and preventing the release of radioactive material beyond permissible limits”
  ”…bring the target station into a safe state in case of an abnormal event from nuclear safety point of view…”

## Slide 4: Pilot TSS
Scenario analysis ongoing (quantitative)
The hazard analysis (qualitative) indicates a set of likely events for TSS => Pilot TSS
TSS
Target Wheel stop during beam on Target
Loss of Target wheel cooling during beam on Target
  Includes loss of flow, loss of cooling function and the He bypass scenarios
Leakage from Target Cooling circuit into monolith, Depressurization of Pcool
Pilot TSS
Selected events

## Slide 5: Pilot TSS: system inputs
Process variable Event | Outlet velocity | Outlet pressure | Inlet temperature | Target shaft rotational speed | Wheel motor power consumption
Loss of He cooling flow (blower fail), #3 | X |  |  |  | 
Loss of He cooling pressure (leakage), #4 |  | X |  |  | 
Loss of He cooling heat exchange, #3 |  |  | X |  | 
Decrease of wheel rotational speed, #1 |  |  |  | X | X
SSZ
PSZ
TSZ

## Slide 6: Pilot TSS: system output
Purpose = achieve safe state
Safe state = no beam on target
Ion source
  Contactors stop allowing power to the Ion source
    Closed if Target variables ok – allow power
    Open if any out of range – no power on 400 V electrical power supply to the ion source
  Contactors dedicated to TSS
RFQ as a remaining potential redundant solution
Conventional electrical power (400 V )
High voltage isolation
High voltage electrical power generation
(75 kV)
Ion source high voltage area
Control
Coils
Magnetron
TSS control

## Slide 7: Pilot TSS: safety functions
Function | Normal operation
TSS shall achieve safe state if… | 
… target He cooling outlet velocity < 40 m/s | 60 m/s
… target He cooling outlet pressure < 7 bar | 10 bar
… target He cooling inlet temperature > 80 °C | 40 °C
… target shaft rotational speed < 11.6 rpm | 23.3 rpm
… target wheel motor power consumption < TBD W | TBD W

## Slide 8: Pilot TSS: safety functions - principal
Read
Target wheel He cooling outlet velocity
Target wheel He cooling outlet pressure
Target wheel He cooling inlet temperature
< 40 m/s
< 7 bar
> 80 °C
If inside all limits
Evaluate
Act
Close contactors at the ion source
If any limit exceeded
Open contactors at the ion source SAFE STATE
If sensor connection lost
If communication lost
If power lost
Target wheel shaft rotational speed
< 11.6 rpm
Target wheel motor power consumption
< TBD W
Diagnostic
If control HW failure
Fail safe

## Slide 9: Pilot TSS: architecture – ESS layout
Target building
Two TSS rooms
Control equipment
Process measurements
Front end building
Beam shut off equipment
150 m
600 m

## Slide 10: Pilot TSS: architecture – Target building
TSS room 1
Control equipment
CPU
Utility room
Process measurements
Distributed I/O
TSS room 2
Control equipment
CPU

## Slide 11: Pilot TSS: architecture – system layout
PSZ
SSZ
TSZ
DI
DI
PLC
PLC
DO
DO
1oo5
1oo5
2oo3
2oo3
2oo3
2oo3
2oo3
2oo3
2oo3
2oo3
2oo3
2oo3
Utility room
TSS room 1
TSS room 2
Front end building
x3
x3
x3
x3
400 V
Ion source
x3

## Slide 12: ESS safety function classification - Public
Severity (mSv) Probability | 0.01-0.1 | 0.1-1 | 1-20 | 20-100 | >100
H1 Normal |  |  |  |  | 
H2 Expected frequency ≥ 10-2 |  | C3 | C2 | C1 | C1
H3 Unexpected 10-4 ≥ frequency < 10-2 |  |  | C2 | C1 | C1
H4 Unlikely 10-6 ≥ frequency < 10-4 |  |  |  | C1 | C1
H5 Very unlikely frequency < 10-6 |  |  |  |  | C1
Unacceptable
Risk reduction recommended
Tolerable
Classification | Severity | Meaning
C3 | Low | Verification + qualification
C2 | Medium | C3 + independant, physically separated redundant trains
C1 | High | C2 + diversity

## Slide 13: Next in design development
Bending magnet control/measurement
  Meet requirement for Operations from Accelerator to allow ion source warm-up and/or beam in accelerator while Target Station not ready for beam
Safety assessment
  Evaluate Pilot TSS design coverage of requirements
Start electrical design
  New electrical engineer working on Target started this month
TSS in main control room
  Determine details of signals to EPICS and to Machine Protection relevant system
  Determine requirements for TSS hardware in MCR
Pilot TSS PDR in December

## Slide 14: End
Thank you

## Slide 15: Pilot TSS events
Events related to
  Target wheel cooling
  Target wheel rotation
Examples from qualitative hazard analysis
4
1 and 3

## Slide 16: Stakeholders
SSM
  Radiological consequences
  Safety classes
  Event classes
  Design principles
ESS
  Safe, reliable, high availability

## Slide 17: Pilot TSS: logical blocks – one train
Read
Evaluate
Act
System
Subsystem
P
P
CCF
DI
CPU
DO
C
C
CCF
Diagn
v
v
CCF
Diagnostic
T
T
CCF
r
r
CCF
P
v
T
r
P
P
CCF
P
Diagnostic
Diagnostic
Diagnostic
Diagnostic