## Slide 1: Progress on Selected Accident Analyses
Per Nilsson, CFD Specialist and Jan Espen Presteng, Safety Engineer
www.europeanspallationsource.se
October, 2015

## Slide 2: Outline
Background
Hazard analyses
First 5 scenarios
Plans

## Slide 3: Background
SSM;
Nuclear Authority
Design Facility
Hazard Analysis
Systems
Buildings
Operation
Events (Severity & Probability)
PIEs and Top
Enveloping
Scenario Analyses
Radiological impact
Inventory
Dose Factors
Safety Functions
Classification
Disciplines: - Mechanical - Ventilation - Electrical …
Physical evolution
Release Factors
Leaks, diffusion
Internal spread
External spread
Unmitigated
Mitigated
Severity Probability | 0.01 -0.1 | 0.1 -1 | 1 -20 | 20 -100 | >100 mSv
H1 Normal |  |  |  |  | 
H2 Expected |  |  |  |  | 
H3 Unexpected |  |  |  |  | 
H4 Unlikely |  |  |  |  | 
H5 Very unlikely |  |  |  |  | 

## Slide 4: Selected events
Enveloping events (to cover all events in hazard analysis)
Unmitigated
The first set shall include diversity of locations and types
Results:
Dose to workers and reference person
Feedback to system design - Classification - Target Safety System TSS - Redesign

## Slide 5: Selected events
Target Wheel stop during beam on target
Beam Event: Focused and non-rastered beam on target
Loss of Target wheel cooling during beam on Target
Leakage from Target Cooling circuit into monolith, depressurisation of PCool
Clogged W channels, local overheating
Loss of He purification function
Water leakage from Intermediate Water System into Target He
Loss of confinement in Target He system – release into Utility rooms
LH2 leakage with explosion/LH2 leakage with local fire
Water leakage in monolith (highest contamination level)
Water leakage into connection cell and utility rooms
NBG/Chopper - missile effect on monolith system
Beam dump – high power beam when target in maintenance mode
Earthquake scenario Target/monolith
Active Cells: Operator inside maint. cell when sliding door unintentionally opens
Active Cells: Operator inside confinement (process cell) next to worst case inventory
Active Cells: Operator inside confinement (maintenance cell) next to worst case inventory
Active Cells: Loss of dynamic confinement (loss of HVAC)
Active Cells: Loss of confinement process/maintenance – open doors
Active Cells: Fire in Maintenance or Process cell
Active Cells: Earthquake scenario

## Slide 6: 18. Ventilation HA
6
6
Severity Public Probability | 0.01-0.1 | 0.1-1 | 1-20 | 20-100 | >100 mSv
H1 |  |  |  |  | 
H2 |  |  |  |  | 
H3 |  |  |  |  | 
H4 |  |  |  |  | 
H5 |  |  |  |  | 
Event
Extraction fan stops
Postulated Initiating Events
External event: electricity supply interruption
External event: earthquake
External event: fire in the fan room or fire in the ducts
Component Failure
Wrong working procedure (collision on the component or wrong installation of the component )
Environment parameters exceed (T, humidity) machine specifications
Process automation failure
P (per year)
6,37E-02
1,00E-06
2,79E-02
1,00E-02
1,00E-04
1,00E-02
Top Events | Unmitigated Consequences
Loss of dynamic confinement Decreased air flow | L: contamination leaks to High Bay and Technical galleries L: leaks in Technical Galleries and Highbay vented outside (reduced filtering)
C to operators | C to Public
>100 mSv Only this considered for HA | < 0.05 mSv
Postulated Initiating Events | 
 | RR
External event: electricity supply interruption | 
External event: earthquake | 
External event: fire in the fan room or fire in the ducts | 
Component Failure | 
Wrong working procedure (collision on the component or wrong installation of the component ) | 
Environment parameters exceed (T, humidity) machine specifications | 
Process automation failure | 

## Slide 7: 18. Loss of Dynamic Confinement in AC
7
7
Physical case investigated based on half sphere, r = 3m
Radiological first estimate to workers in 4h 190 mSv in High Bay 130 mSv in Galleries
Severity > 20 mSv
Other mitigations! E.g. PSS
Safety Functions:

## Slide 8: 15. AC Prompt Radiation To Worker
Physical case investigated
Doses (obvious?) workers: severe public: no impact
Mitigations, highest class Control systems Procedures

## Slide 9: 9. Hydrogen combustion, 2 cases
b. Slow combustion
- Internal physical case being investigated (first rough estimate 0.5 kg Tungsten oxidised)
- Releases to be calculated
a. Explosive
- External physical case investigated
(severe but not radiological)
- Releases to be calculated
WSP

## Slide 10: 8. Large Leak From Target Helium
Physical case investigated Filter backflow and wheel effect separate, for now (ODH immediate problem for workers)
Doses being calculated, current estimates: workers: even <100 g/s severe public: full rupture < low severity

## Slide 11: 1. Wheel Stop With Beam
Physical case investigated up to event, i.e. mitigated Result: Maximum 4 pulses ( ~ 0.28 s)
Unmitigated to be analysed
Releases to be calculated

## Slide 12: Plans
First 5 accident scenarios by Dec 2015
  Scenario development (evolution, impact), 20th Oct
  Dose rate calculation
  Approval completed, 14th Dec
All scenarios ready by May 2016