## Slide 1: The journey to maintenance effectiveness 5th Asset & Maintenance Management Workshop ESS – Lund
M.Chiodi, D. Gain / CERN - EN-CV
28.09.2023

## Slide 2: The Cooling & Ventilation Group (CV) at CERN
The CV Group is responsible for the design, installation, commissioning, operation and maintenance
of the industrial ventilation, pumping stations, cooling and fluid distribution systems for all accelerator complex and its experimental areas.

## Slide 3
For over 30 years, the CV Group
has been using an Enterprise Asset Management System
to manage, plan and monitor its day-to-day operation and maintenance activities
through the installation’s life cycle.

## Slide 4: EAM tools used
EAM Light
CERN

## Slide 5: CV EAM usage and numbers
Equipment inventory/tracking
Maintenance & works management
Spare parts management
Documents management (EDMS)
Contracts management
Statistics

## Slide 6: CV EAM usage and numbers
Equipment inventory/tracking
Maintenance & works management
Spare parts management
Documents management (EDMS)
Contracts management
Statistics
Users | 148
CV members | 80
External Contractors | 68
Objects | 
Assets | 4 765
Functional Positions | 128 886
Systems | 1 986
Work Orders | 
Work Orders registered | 260 000
Work Orders processed / year | 8 000
Spare Parts | 
Spare Parts catalogued | 20 000
Spare Parts in Store | 132 000
Documents | 
Linked Documents | 40,835

## Slide 7: Equipment implemented in EAM over the years
Chart: Functional Positions in EAM
| 36526 | 40179 | 43831 | 44927
equipment | 18000 | 40000 | 105000 | 128886

## Slide 8: Equipment implemented in EAM over the years
Chart: Functional Positions in EAM
| 36526 | 40179 | 43831 | 44927
equipment | 18000 | 40000 | 105000 | 128886

## Slide 9
AS
IS
Structures not homogeneous
Different coding used depending on the generation of the installation
Inventory of some installations not fully implemented
Criticality not implemented
Maintenance procedures to create / review

## Slide 10
Structures not homogeneous
Different coding used depending on the generation of the installation
Inventory of some installations not fully implemented
Criticality not implemented
Maintenance procedures to create / review
AS
IS
Daily usage of the tool not smooth
Installations data extract not straight forward
Historical data not easily accessible
KPI reporting not automatised
Breakdown analysis difficult to perform
Maintenance tasks not fully performed by the contractors

## Slide 11
Overcome current CMMS limitations with homogeneous, standard and complete data
Set up specific and standard functional hierarchies
Specify and implement new maintenance task plans including criticality ranking
Improve maintenance contractors' performance monitoring
Ease data exploitation (budget, ISO50001, maintenance reports, etc…)
Structures not homogeneous
Different coding used depending on the generation of the installation
Inventory of some installations not fully implemented
Criticality not implemented
Maintenance procedures to create / review
AS
IS
TO
BE

## Slide 12
AS
IS
TO
BE
EAM
re-engineering project

## Slide 13
maintenance effectiveness
EAM
re-engineering project

## Slide 14: The project road map
Analysis of the existing systems
New hierarchical structures HxGN EAM + (Relationship)
    System / Parent Positions / Positions - Assets
Filtering criterias (Class / Categories)
Installations criticality study & ranking
New maintenance tasks including failure analysis study results (Préventive vs conditional)
Spare parts management policy & equipment material list
« Maintenance Route » adjustment (due to new structures)
Review of the preventive maintenance scheduling
Annual launch of maintenance work orders (Gantt planning)
KPI’s and continious improvement (PDCA)

## Slide 15: System structure Ex: Air treatment B367 – P&ID
5 different Systems:
Ventilation and smoke extraction system
Air handling unit + cooling element water supply
Chilled water production unit + distribution circuit
Power & control electrical cabinets
Process Control Architecture

## Slide 16: System structure Ex: Air treatment B367

## Slide 17: In the EAM Light tool

## Slide 18: System classification
#1 - Type of « Process »
Fluids:
    Raw water
    Cooling water
    Hot water
    Gas
    ...
#2 – Primary function
  Air treatment:
    Clean room
    Electrical sub-station
    Tertiary
    Technical building
    Machine
    IT room
    Technical galllery
    ...
Ventilation:
    Air handling unit
    Air extraction unit
Hydraulic:
    Production
    Distribution
    Production & Distribution
    Sump
    Waste water pit
    ...

## Slide 19: Parent position structure Ex: Cooling Towers B255

## Slide 20: Parent position structure

## Slide 21: CMMS hierarchy details
Location / System / “Top Parent” / Parent Position
Parent Position / Position or Asset

## Slide 22: Parent position classification
#1 - Type of « Process »
Fluids:
    Raw water
    Cooling water
    Chilled water
    Mixed water
    Demineralized water
    Hot water
    Gas
    ...
#2 – Function performed
  Air treatment:
    Ventilation simple flow unit
    Ventilation double flow unit
    Déshumidification Unit
    Ventilation extraction unit
    Air Mixing unit
    ...
Hydraulic:
    Production
    Distribution
    Production & distribution
    Sump
    Waste water pit
    Cooling tower
    Water filling panoply
    …

## Slide 23: Sorting easily…
Systems:
Hydraulic / Ventilation / Electric
Function performed by the systems
Physical machine location (surface / underground / surface for underground)
Acronyms designed for easy searching
A standardized description of systems and parents

## Slide 25: Relationship between objects
Event historic:
Location
Primary System position
Secondary System position
Parent position
Dependent
Budget:
Cost Roll-up
Working together:
Powered by...
Controlled by...

## Slide 26: Criticality definition

## Slide 27: Conclusions
First phase observations:
Operation requirements need to be challeged due to CMMS implementation constraints;
Be focused on our final needs;
It takes some iterations to define correctly the classification criterias;
Consider «Systems» as sets of functions not equipments.
Project is progressing…
Definition of the functional structure standard rules – Done
Implementation of the new «phylosophy» is on going – It takes more time than expected…
Defining the criticality criterias specific to our of facilities;