## Slide 1: Cryogenic System
ESS System Acceptance Review SAR4
4th February 2025
PRESENTED BY Philipp Arnold / Henry Przybilski

## Slide 2: Agenda
1 Scope description and status
2 Documentation, CIDLs and CRs
3 NCRs and other known issues
Applicable codes and compliance
5 Tests pre and post beam
6 Start up checklist
7 Earlier recommendations

## Slide 3: Cryomodules and Distribution System
ACCP
CBX
DTL(5)
Spoke(13)
MBL(9)
HBL(21)
RFQ
ISrc
LEBT
MEBT
HEBT
Dump
Target
Accelerator
CryoPlant
Valve boxes
Normal Conducting Linac
Super Conducting Linac
Cryogenics for the Super Conducting Linac in a nutshell
ACCP
WCS

## Slide 4: Accelerator Cryoplant
ACCP
CBX
…and auxiliary systems
ACCP
WCS
4
TICP
WCS
Rec
Sys

## Slide 5: Documentation, CIDLs, CRs
Main documentation of ACCP and CDS
CIDLs for ACCP and CDS in CHESS as verified
CIDLs for CM (see SCL cavities talk – Cecilia Maiano)
ACCP/CDS docu complete, all CIDLs, 1 CR for CMs closed
✅
✅
✅
✅

## Slide 6: NCRs and other known issues
No open NCR for ACCP and CDS, they are all closed now.
No open NCR for CM. NCR raised during SAT and installation are closed.
Some issues on Cryo that need work
      BCP testing as HP compressor  test planned in week 7/2025
      BCP and HP compressors cannot seamlessly be swapped  improvement project planned until summer 2025
      BCP cannot yet operate as SP compressor  piping changes in summer break
      Cold compressor full spare cartridges and upgrade to AMB outstanding
      Operational issues (CC inlet filter, 80K adsorber regeneration, etc)
several issues on Cryo controls, for instance
      No redundant PSUs in CDS/CM cabinets
      No redundant level controllers
      ACCP controls running on a legacy system with hardware approaching its end of life
      Glitches in the Controls Network for remote monitoring and Alarms handling
…being worked on, no show stoppers at the moment

## Slide 7: Safety of cryogenic systems operations
  SCL commissioning risk assessment ESS-5493839 (for OHS)
  Risk assessment for pressurisation of Cryo ACCP, TMCP, TICP according AFS 2017:3 ESS-4973360 (for QC)
  Risk assessment for pressurised systems according to AFS 2017:3 for CDS and CMs ESS-5003254 (for QC)
  Area Hazard Analysis of cryo buildings (HCB, CXH, CTLG) ESS-0104828
  Task risk assessment cryogenics operations ESS-3153113
  Summary of Safety Helium Collector ESS-5461033
  Summary and sizing of the Linac CDS pressure safety devices ESS-0101321
  Elliptical cryomodule Safety relief device sizing ESS-3231794
  Cryogenic Safety Review (8 June 2016) for spoke safety device design
Cryogenics safety and particular focus on pressurised equipment

## Slide 8: Applicable codes and compliance
- Cryogenics Electrical Cabinets maintenance manual ESS-5585959 according to template ESS-3585736 following
  Swedish Electrical Safety Act (SFS 2016:732)
  ELSÄK-FS 2022:3
  ELSÄK-FS 2022:1
  CDS / CMs pressurised equipment maintenance manual ESS-5585925 follows
  Operation and control of pressurised equipment AFS 2023:11
  ESS rules for principles for in-service inspection ESS-0053218
  ESS procedure for performing in-service inspection ESS-3218570
  All cryo pressurised equipment is registered in EAM
And how this effects our operation and maintenance

## Slide 9: Continuous activities
Technically, Cryo activities are tied to cold SCL and not to beam
- Validation tests performed prior to cooldown
- Monitoring of system health at all time
- CM cryogenics performance
  Heat load measurements at different time (periodically)
  Optimisation of control system parameters (continuous task)
  Integral monitoring (across discipline, for instance vacuum levels)
  Continuous improvements on cryo controls on CMs / CDS and ACCP

## Slide 10: MCR docs and communication
Check list, docs, olog entries…
CDS and Cryomodules
  ESS documents
    Checklist for both CDS and CMs (https://confluence.ess.eu/display/AO/2024+Beam+Commissioning+up+to+BeamDump+%3A%3A%3A+Pre-Start+Checklists)
    Subset of Cryo related alarms are in the LCR alarms configuration (Cryoplants + CMs)  monitored by MCR unless otherwise communicated during the day
    Test reports (Cryo, ICS, SRF) and instructions in CHESS
    Daily communication with MCR
    Olog entries with instructions

## Slide 11: Earlier recommendations
Last review was the Cold coupler conditioning review (CCCR) before cooling down the SCL
Last remaining recommendation is a burst disc exchange procedure which is now drafted and in approval workflow in CHESS: ESS-5587333
Recommendations for CDS IRR and TRR all closed
Earlier recommendations not relevant anymore as systems are in ”as validated” state and fully functional
First time SAR for Cryo

## Slide 12: Finish presentation