## Slide 2: ACC PSS, ACC ODHDS & CB ODHDS
System Acceptance Review 5 (2025-02-04)
PRESENTED BY Morteza Mansouri
2025-01-31

## Slide 3
1
ACC PSS

## Slide 4: ACC PSS: Scope and status












X
X
The modulator for HBL-040 has been replaced. The ACC PSS interface with the modulator is re-installed, awaiting retest during weeks 6 & 7.
The ACC PSS integrated test with REMS is planned for maintenance days in weeks 8 & 9.

## Slide 5: ACC PSS: current status




See back-up slide
Another rev. is required following the REMS test
Post implementation review in the Risk index for Accelerator (ESS-3878402) should be completed by ACC







Work in progress to prepare by SAR5 in EAM


## Slide 6: ACC PSS: non-compliances (ESS-5547527)

## Slide 7: ACC PSS: non-compliances
Item | Comment
Non-compliances from the ACC PSS HWSAT report (ESS-5355848) | All critical items are addressed. Some equipment still missing the complete set of lables. see ICSPSS-5678
Non-compliances from the ACC PSS CDR report (ESS-5121803) | All critical items are addressed. The remaining items are the following: Two minor improvement to the ACC PSS SIL assessment Order spares for safety tokens Improve the quality of Risk index for Accelerator (ESS-3878402) by adding relevant reference analysis documentation (for accelerator division) See ACC PSS CDR Follow-up

## Slide 8: ACC PSS: non-compliances
Item | Comment
Non-compliances from the ACC PSS SW peer-review report (ESS-5244740) | All critical items are addressed. The remaining items are the following: Improve quality of ACC PSS & Gamma Blocker ICD (ESS-3231606) Consider the proposal on how to implement ACCPSS_SIF6 See ICSPSS-5680
Non-compliances from the ACC PSS FIT report (ESS-5572436) | The critical remaining items are the following: Integrated test with REMS: The test shall be done prior to BoD. It is planned for maintenance days in weeks 8 & 9. Installation of mirrors between the beamline and northern wall of the tunnel to facilitate search: Installation is ongoing and will be completed in weeks 6 & 7. Improvement of lighting between beamline and the northern wall of the tunnel to facilitate search: Approval from RP to keep temporary lights during BoD operation. Permanent lighting will in place prior to BoT. See ICSPSS-5679

## Slide 9: ACC PSS: CCRs & further improvements
Item | Comment
Reverification of ACC PSS interface with HBL-040 modulator | The interface box is re-installed, awaiting retest during weeks 6 & 7. CCR ESS-5594536
Improve the occupancy counter function of ACC PSS | The occupancy counter of ACC PSS is automatically reset to zero upon losing integrity of access control to the area (e.g. an e-exit door is open). The reset will done manually to enable operators reset the counter considering the access status, and number of individuals still in the tunnel. The update is planned for weeks 6 &7. See ICSPSS-XXXX
Address issue with PAS | We have recently observed issues with person stuck inside PAS during entry or exit cycles. PAS sensors will be adjusted to improve the situation. The update is planned for weeks 6 &7. See ICSPSS-xxxx

## Slide 10: ACC PSS: CIDL
See OS-0000011

## Slide 11
2
ACC ODHDS & CB ODHDS

## Slide 12: GDS: CB ODHDS & ACC ODHDS

## Slide 13: ACC ODHDS & CB ODHDS status








Action items are addressed. See ACC ODHDS CDR Follow-up
Work in progress to prepare maintenance specs in EAM by SAR5

## Slide 14: ACC ODHDS & CB ODHDS: CIDLs
For CB ODHDS see OS-0000091
For ACC ODHDS see OS-0000092

## Slide 15: Thank you! Questions?

## Slide 16
Back-up slides

## Slide 17: ACC PSS: FSA findings

## Slide 18: ACC PSS: FSA findings

## Slide 19: ACC PSS: FSA findings