## Slide 2: Achieving a Balanced Radiation Safety Case for the ESS Target Station
PRESENTED BY Linda r. coney

## Slide 3: Agenda
1 ESS Radiation Safety Framework
2 ESS Target Station: Radiation Safety Case
3 How did we get here?
4 Questions?

## Slide 4
ESS Radiation Safety Framework
1

## Slide 5: Radiation Safety Analysis Purpose
Protect ESS workers and the public from potential radiological consequences
  Apply a systematic process to identify, evaluate, and control potential radiation hazards related to ESS areas.
  Identify hazardous conditions and events associated with the facility processes, operations, work activities, and natural phenomena
    High power beam impacting the tungsten target will create an inventory of nuclides
    3000 kg of tungsten, 5 MW proton beam, 5-year target wheel lifetime
  Understand potentially hazardous conditions and scenarios
  Define necessary prevention and mitigation measures
    Input to system design requirements – Target systems, ACC systems, Instruments, waste management, building features, shielding, HVAC, Controls, PSS, TSS
    Identify need for radiation safety functions
  Identify g evaluate g control these hazards

## Slide 6: Engineering & Analysis 7-Steps
Radiation Safety Analysis & Classification with deliverables
Step 1
Define the space
Define how you want to use it
Describe it, design it
Step 2:
Identify sources
Propose area classification
Characterize hazards
Concepts of Operations
System Descriptions
Area classification for design
List of sources (prompt, residual, contamination)
Shielding design
Prompt dose rates
Activation calculations
Inventories, DAC levels
Step 2-3 Analysis Reports
List of RSF, WRSF, AM, SSC
ESS Categorization report
Many SSC classification reports
Many AAP & AAW reports
Step 6:
RSFs – Operational Group
WRSFs for workers (DID L1 & L2)
SSC classification for radiation safety
(mechanical, electrical/I&C, HVAC, civil, lifting)
Step 7:
DID
Step 3:
Define RSFs for public, assign systems
Define WRSFs, assign systems
(DID L1 & L2)
Define source term for public
Do conditions meet the proposed area classification limits?
Step 6:
Safety Group RSFs
SSC classification
Step 4-5:
Hazard Analysis –> Bounding events
Event analyses for public
Define Safety Group RSFs
Event analysis for worker safety
New WRSFs (DID L3)
DID analysis reports
Step 5.5:
Barrier integrity Assessment
Step 5.7:
Define Safe State
Barrier int. report
Safe state report

## Slide 7: Engineering & Analysis 7-Steps
Step 2:
Identify sources
Propose area classification
Characterize hazards
Concepts of Operations
System Descriptions
Area classification for design
List of sources (prompt, residual, contamination)
Shielding design
Prompt dose rates
Activation calculations
Inventories, DAC levels
Step 2-3 Analysis Reports
List of RSF, WRSF, AM, SSC
ESS Categorization report
Many SSC classification reports
Many AAP & AAW reports
Step 6:
Safety Group RSFs
SSC classification
DID analysis reports
Barrier int. report
Safe state report
Step 4-5:
Hazard Analysis –> Bounding events
Event analyses for public
Define Safety Group RSFs
Event analysis for worker safety
New WRSFs (DID L3)
Step 6:
RSFs – Operational Group
WRSFs for workers (DID L1 & L2)
SSC classification for radiation safety
(mechanical, electrical/I&C, HVAC, civil, lifting)
Step 5.7:
Define Safe State
Step 5.5:
Barrier integrity Assessment
Step 7:
DID
Step 3:
Define RSFs for public, assign systems
Define WRSFs, assign systems
(DID L1 & L2)
Define source term for public
Do conditions meet the proposed area classification limits?
Step 1
Define the space
Define how you want to use it
Describe it, design it
Radiation Safety Analysis & Classification with deliverables

## Slide 8: Engineering & Analysis 7-Steps
Step 2:
Identify sources
Propose area classification
Characterize hazards
Concepts of Operations
System Descriptions
Area classification for design
List of sources (prompt, residual, contamination)
Shielding design
Prompt dose rates
Activation calculations
Inventories, DAC levels
Step 2-3 Analysis Reports
List of RSF, WRSF, AM, SSC
ESS Categorization report
Many SSC classification reports
Many AAP & AAW reports
Step 6:
Safety Group RSFs
SSC classification
DID analysis reports
Barrier int. report
Safe state report
Step 4-5:
Hazard Analysis –> Bounding events
Event analyses for public
Define Safety Group RSFs
Event analysis for worker safety
New WRSFs (DID L3)
Step 6:
RSFs – Operational Group
WRSFs for workers (DID L1 & L2)
SSC classification for radiation safety
(mechanical, electrical/I&C, HVAC, civil, lifting)
Step 5.7:
Define Safe State
Step 5.5:
Barrier integrity Assessment
Step 7:
DID
Step 3:
Define RSFs for public, assign systems
Define WRSFs, assign systems
(DID L1 & L2)
Define source term for public
Do conditions meet the proposed area classification limits?
Step 1
Define the space
Define how you want to use it
Describe it, design it
Radiation Safety Analysis & Classification with deliverables

## Slide 9: Achieving the Operation License
How do we do this?
  Demonstrate
  That we understand the radiation hazards for the facility.
  That we have identified the necessary radiation safety functions to manage them.
  That we have properly implemented the systems to execute those functions.
    The systems meet the requirements defined by the analyses (functions, classification, reliability, quality, withstand appropriate loads, etc.).
    The systems follow ESS design rules.
  Meet the SSM conditions (regulator re. radiation safety)
    Rules for radiation safety analysis, facility design, barriers, system design, analysis, etc.
  Follow the ESS processes -> deliverables -> develop systems -> verify safe facility -> meet conditions
    Radiation safety analysis & classification, ESS design & development, Radiation protection

## Slide 10: ESS Licensing
  Introduction
  Scope
  Site description (Tech)
  Facility description (Tech)
  Basic radiation safety principles (ESH)
  Organisation, governance and management of practices (WoW, Tech)
  Protection of workers (ESH)
  Protection of the general public and the environment during anticipated operations (ESH)
  Radioactive waste, decommisioning and costs (ESH)
  Emergency preparedness (ESH)
  Design and assessment (Tech/ESH)
  Mechanical devices (Tech/Q)
  Physical protection (ESH&S)
  Information security (ESH&S)
  Operations (OID/Tech)
  Facility safety (RSTF, 7-steps) (Tech)
More than rad safety analysis – cSAR has 16 chapters
Scope split between ESH& Security part of the organization, Technical Directorate, Operations – ALL are involved & important
Alignment across areas is critical and complex

## Slide 11: Connections from Radiation Safety Analyses
  Operational Limits & Conditions (Ops)
  Facility monitoring (Ops, RP)
  Maintainability
  Operability
  Safe state determination (ESH&S)
  Procedures to reach safe states (Ops)
  Emergency management (ESH&S)
  Security (ESH&S)
  Radwaste (ESH&S)
Impact on/feedback from other areas

## Slide 12
ESS Target Station: Radiation Safety Case
2

## Slide 13: What areas are involved?
Neutron source, waste management – all of D02
D02

## Slide 14: Key Features of the ESS Target Station
Neutron Factory
proton beam
proton beam window
proton beam instrumentation plug
Moderator and reflector
target wheel
neutron beam extraction port
monolith vessel
target monitoring plug
Helium cooling of target material
Mass flow 3 kg/s
Pressure 11 bar
Temperature inlet/outlet 40 °C/ 240 °C
Rotating solid tungsten target
36 sectors
Mass, total 11 tonnes, including 3 tonnes of W
Rotates 23.3 rpm, synchronized with pulsed proton beam 14 Hz
Moderators
Provisional locations of moderators above and beneath the target wheel, i.e. monolith centre
1st MR plug exploits the upper space, offering:
  Cold, 30 mm high, liquid H2 moderators, 17 K
  Thermal, 30 mm high, H2O moderator, 300 K
Diagnostics and instrumentation
Controlled and integrated commissioning and operation of the accelerator and target
Fluorescent coating of PBW and target front face
Optical paths, grid profile monitor, aperture monitor
Wheel monitoring including position, temperature, vibration, as well as internal structure
Target Safety System
Monitors target coolant flow, pressure and temperature, monolith pressure, & target wheel rotation
Prohibit beam on target if parameters are outside limits
Step 1

## Slide 15: Key Features of the ESS Target Station
Remote Handling
Utilities and cooling plant
Helium cooling of target wheel
Water cooling of moderators, plugs and shielding
Intermediate water loops between primary circuits and conventional facility utilities
Helium cryoplant for cold moderator system
Nuclear grade HVAC system
130 m
22 m
37 m
High Bay
Transport hall
Remote handling systems
Large active cells for safe storage and processing of spent radioactive monolith components
Shielded casks for transfer of spent components from monolith to active cells
D2T (drift to target)
NF monolith
Utilities block
Active Cells Facility
proton beam
Step 1

## Slide 16: Radiation Hazards & Safety Provisions for Public
Public – Neutron Factory
Prompt:
  Shield: Civil structures, monolith shielding (permanent & removable), beam drift room shielding
  Residual:
  Shield: same as for prompt + casks
  Limit monolith component irradiation time – replacement schedule (AM)
  Decay time for monolith components (AM - maint)
  Contamination
  Limit irradiation time – monolith component replacement schedule (AM)
  Water: Decay gas in GLS before release (AM – maint), exchange primary water before tritium limit (maint)
Radiation Safety Functions (RSF) and Administrative Measures (AM)
  Contamination
  Tungsten, helium
    Maintain source temperature:
      Distribute beam on target wheel – raster magnets for beam modes that require it
      Rotate wheel
      Cool target wheel & tungsten (helium cooling systems – system 1010)
      Purify helium (1010, 1015)
      Stop beam delivery to protect wheel – Machine Protection System of Systems (MPSoS) (L2)
    Confine helium (1010, 1015, pressure control, sensing lines)
Step 2-3

## Slide 17: Safety Provisions for Workers
Workers – Neutron Factory
Prompt:
  Shield: around primary water systems
  Access control in utility block (WO, training)
  Control access based on radiation level (RP team, WO, procedures, monitoring)
  Prevent proton beam if workers in specific areas & prevent access when beam on target (L1 WO, procedures) (L2 PSS)
  Residual:
  Shield: add local shielding for water systems, ion exchange columns, spent resin
  Decay time for water – delay tanks
  Decay time for ion exchange spent resin (WAM - maint)
  Replace helium system filters, primary water components
  Control access based on radiation level
  Prevent access if beam on target, prevent beam on target if workers in area (water) (L1 WO, procedures) (L2 PSS)
Worker Radiation Safety Functions (WRSF) and Administrative Measures (WAM)
  Contamination:
  Control access based on contamination level (RP team, WO, monitoring)
  Water
    Confine primary water & ion exchanger resin
    Purify primary water
    Controlled release from monolith (L1 vessel and extensions, vacuum, off-gas extraction system)
    Confine unforeseen leakage (L2 building with floor drains, drain tanks, vessel, HVAC)
  Tungsten, helium
    Controlled release from monolith (L1 vessel, etc)
    Controlled release from rooms (L1 civil structure, HVAC)
    Control leakage (L2 monolith vessel & pressure relief system, helium pressure relief system, building, HVAC)
Step 2-3

## Slide 18: Anticipated Operations – Area classes
Identify & characterize hazards (prompt, residual, contamination)
Production mode
Maintenance mode:
monolith closed
Maintenance mode:
Connection Cell work
Step 2-3

## Slide 19: Bounding Event Analyses – Neutron Factory
Barrier-P/R-1: permanent & removeable shielding, civil structure around monolith
Barrier-T-1: tungsten bricks
Barrier-T-2: target wheel shroud, primary helium cooling system and associated confinement SSCs
Public
  Safety Group required for stopped wheel and loss of cooling for tungsten:
    Target Safety System (TSS) required
  TSS also in global events that may initiate AA1P or AA3P: fire, lightning
Workers
  Helium, tungsten: evacuate for helium leaks, isolate purification system before access (maint)
  Water: evacuate for leak (maint)
  Prompt: PSS detect intrusion & stop beam, emergency beam-off buttons in utility areas
Assessments identify where additional safety provisions are required
Step 4-5
Step 5.5

## Slide 20: Neutron Factory - classified SSCs (Public)
  No classification for shielding SSCs
Structures, Systems, & Components
Step 6

## Slide 21: Defense in Depth
  Neutron Factory – public
  Basic principles with respect to the public
    Attenuate prompt radiation with shielding
    Attenuate residual radiation with shielding
    Maintain target tungsten integrity
    Stop proton beam if process parameters are off-normal process – limit tungsten damage
  Single level of DID (L1) sufficient to manage prompt & residual radiation
  Three levels (L1, L2, L3) for contamination hazards due to activated target tungsten
  Safety Group required – one system (TSS)
  No Consequence Mitigating Group (L4)
Neutron Factory – workers
  All functions for public and:
  Worker presence allowed or prohibited depending on the mode & area
  Three levels (DIDW-L1, L2, L3)
  DIDW-L1, L2 access control for prompt & residual hazards
  DIDW-L1, L2, L3 excludes beam on target or presence of workers in high class area
  DIDW-L1, L2, L3: contamination hazards from target tungsten and cooling media (helium and water)
Structures, Systems, & Components
Step 7

## Slide 22
How did we get here?
3
And you may find yourself in a beautiful house
And you may ask yourself, “Well, how did I get here?”
Letting the days go by… Once in a Lifetime, Talking Heads (1980)

## Slide 23: License to Operate – INP NOW
A step wise approach to routine operation license
Siting permit
Submission Jan 2012
Received Jun 2014
Installation permit
Submission May 2016
Received Oct 2017 excl. NSS and H09 (rad waste)
Trial operation permit NCL
Submission Jul 2019
Received Oct 2020
Routine operation permit
Submission TBD
Received TBD
Installation permit NSS & H09
Submission Mar 2022
Received Sept 2022
Trial ops permit SCL
Submission Oct 2023
Received May 2024
Extension for new Instruments
Trial ops permit BOT, NSS, H09
Submission Dec 2024
Received Feb 2026
INP = Intentional Neutron Production

## Slide 24: ESS Radiation Safety
  September 2019 – Radiation Safety Task Force
    Clarify & implement the ESS radiation safety analysis approach, RSF/WRSF ID, and SSC classification
    Update existing analyses, execute complementary analyses, and manage RSF/WRSF identification
  RSTF Team
    Core team representing broad technical expertise and all facility areas of interest: Accelerator, Target Station, ICS, NSS, ESH, RadWaste, Building/Facility, Quality
    Additional specialty resources: power supply,HVAC, Radiation Protection, rad monitoring, shielding, fire, mechanical components, engineering, security
  Outcome & goals
    Develop & implement 7-steps for SCL application
    Align across facility
  Evolved through INP application (for BOT) (2025)
A little history

## Slide 25: Balancing Time, Energy, Impact
  Started with and spent significant time/energy on accident analyses
    Built in structured Step 2-3 later
  Early applications reported everything
  Disproportionate time and text on event analyses – majority for Public resulted in acceptable risk
    Public – we have 31 AAPs for ESS
      4 require Safety Group RSFs (TSS)
      5 with limited duration (>24 h) (shielding)
    Workers – 38 AAWs, 21 defined new WRSFs
  Start with normal ops
    Define what you will have, what you need when things go right
    L1 functions and SSCs are the foundation
  Event class is critical, can be complex
  Be clear on purpose/intent/strategy for radiation safety analyses for design
    ex: AAs not intended to be realistic, rather deterministic
    Exaggerated the impact – if ok, then done
    Risk to apply these analyses to other purposes, it could result in overconstraints
Consider carefully where to devote resources

## Slide 26: Connect with Operations
  Clear about the radiation safety process
    Well-understood interplay with facility design & requirements for classification
    Design requirements align with ESS rules
  Less clear what it meant for Operations
    Still working to communicate this
    Operational Limits & Conditions (OLC)
    Track maintenance – EAM/MCR tools
    Significant overhead, especially for public safety SSCs
  Get feedback to/from Operations ASAP
    Establish an outline of planned ops and maintenance procedures
    What is the envisioned approach? How often? Who?
  Avoid untested or limited lifetime tech
    Clever use of other SSCs
    Bigger workload on analysis – easier on ops
  Define needed, not nice to have
  Build in flexibility
    Conservative assumptions reduce reliance on them
    Tough to track impact of assumptions
    Eg. Don’t rely on HVAC in AAPs, unless it makes it worse!
Plan for operations along with design – easier earlier

## Slide 27: Optimize the Safety Case
  After SCL, re-examined safety case with respect to the public
  Applied knowledge gained in later steps back to Step 2-3
  Narrowed the focus – identified what is important for the public and what is not
  Shifted away from default to RSF, instead define what it means to be an RSF
  Impact on Operations re. public SSCs
  Applied for Accelerator, Target Station, and NSS
  ACC:
    Distilled MPS functions to essentials
      Pared down MPS/beam instrumentation – no BLMs, no GRID, no optical system
      Align beam destination w/beam parameters
      Beam loss: only beam current monitors for A2T losses
      Monitor raster magnets, wheel rotation, synchronisation, helium cooling parameters
    Removed water systems
  Neutron Factory water systems, HVAC – only for workers (ACF HVAC still for public)
  NSS: only permanent shielding for public
  General – defined minimum required SSCs to execute functions
Focus on essentials – clarify public vs workers safety case

## Slide 28: Map to Defined Operations Plan & Parameters
  Safety case for 5 MW
    Demonstrate facility built for full capability
  Early commissioning (especially) not near max power
  What is the difference?
    Different beam configurations
    Different inventories
  Causes confusion re. what is required for early commissioning vs for 5 MW
  Sensitivity studies for lower beam power
  Define when functions are needed
    From the start? After 1 year? After 2 MW?
    Tie into facility modes – eg. Production vs Maintenance
  Be clear about descriptions for how the facility is operated as a user facility vs commissioning
  Define parameters tied to activation calculation in useful units (e.g. MWh)
  Don’t just check the worst… find the bottom edge – ‘bounding for not needed’
Help Operations and system owners know when functions & SSCs apply

## Slide 29: Thank you for listening – Questions?

## Slide 30: Engineering & Analysis
Radiation Safety Analysis & Classification
Step 1: System/facility description, Concept of operations including modes of operation
Step 2: Identify & characterize radiological hazards (prompt, residual, contamination) in operations
Step 3: Identify Radiation Safety Functions (RSFs) and Worker Radiation Safety Functions (WRSFs), Administrative Measures (AM) for normal operations & maintenance
Step 4: Accident/event analysis
  List of events to consider with event class (ranking from H2 to H5, high to low frequency)
  Potential impact of event on workers and public
  Bounding events based on previous list and assessment
  Quantitative impact on public and workers
Step 5: RSF and WRSF identification from accident analyses
    Step 5.5: barrier integrity
    Step 5.7: define facility safe state
Step 6: RSF categorization and SSC classification by sub-discipline
Step 7: Defence in Depth (DID) – justification of independence of DID level

## Slide 31: Bounding Event Analyses – ACF
Public
Workers
Assessments identify where additional safety provisions are required

## Slide 32: Connections/impact for Target Division
How does all of this affect our work?
  Testing
    Verify compliance with requirements – functionality, reliability, ability to maintain
    Manage noncompliance – Licensing team, SSM
  Change control
    Any changes to the SSCs, ways of working (e.g. operations procedures, radwaste storage) need to be assessed from the perspective of radiation safety.
  Ways of working as we evolve toward Commissioning/Operations
    Safety case defines (Step 1, 2-3, 4-5) how we plan to do things
    Defines RSF/WRSFs required during different modes (Production/Cooling down vs. Maintenance/Start-up)
  Demonstrate how to manage radiation hazards to workers during maintenance activities
    Record knowledge/experience gained during testing – try things out now when its ‘easy’

## Slide 33: Connections/impact for Target Division
Change control
  Neutron Factory – Helium leak rate
  NF, RH – reference document changes (1st, 2nd order)
  Operations
  NF – mode transitions
Ways of working
  RH – Location of workers
  Level of inventory
  NF – circulate/purify He before transition to Maintenance mode
  NF – exchange water
  NF – radwaste leaves D02
  RH – wait 14-days before remove monolith component
  RH – wait before cutting, nothing else when cutting
  System lifecycle
  SARs (System Acceptance Review)
  SSR5 (Safety Readiness Review 5)
Examples

## Slide 34: Operations/Maintenance constraints
Transition between Neutron Factory modes
NF modes |  |  |  | 
Production | Prompt radiation Higher, circulating fluid inventories |  | Reduced access PSS rooms locked | 
Cooling Down | Remove residual heat Purify helium, then depressurize |  | Maybe open basement earlier | 
Maintenance | Lower, relocated or removed fluid inventory |  | Access allowed everywhere Need special monitoring for water, helium leak | 
Startup |  |  |  | 

## Slide 35: Prep of references & cSAR
Important to:
  Pay attention to Quality – content & document quality
  Templates!
  Do not underestimate the time needed to perform analyses, review them, incorporate them into the cSAR
  Bring on board documentation/writing specialists
  Assign someone to be responsible for checking alignment across areas
  If you have different areas with different levels of hazard, do scoping calculations to allow focus on the most critical areas
  Don’t just check the worst… find the bottom edge – ‘bounding for not needed’