## Slide 1: Target HVAC system at the ESS research facility and its role in neutron production
PRESENTED by ANNA BIELIAIEVA
NUCLEAR VENTILATION ENGINEER
System owner target hvac and off-gas systems

## Slide 2: ESS overview

## Slide 3: Target building (D02)

## Slide 4: Target station overview
Target Station volume:≈75000 m3 (High Bay 45000 m3);
Number of rooms: ≈50;
Presence of airborne contamination/air activation (Active Cell, Utility Rooms, Connection Cell);
Presence of toxic (hypoxic) gases (Hydrogen room, Utility rooms, Connection Cell);
Presence of explosive gases (Hydrogen room).

## Slide 5: Target HVAC system function for neutron production

## Slide 6: Contribution to confinement function

## Slide 7: TS HVAC Design

## Slide 8: TS HVAC subsystems
=ESS.TS.ISS.G01
Environment Monitoring System:
=ESS.TS.ISS.G01.B01 1130 Environment Monitoring System – pressure, temperature and humity
Ventilation systems:
=ESS.TS.ISS.G01.G01 1131 Air supply for zones C1, C2 and C3 (technical gallery)
=ESS.TS.ISS.G01.G02 1132 Air exhaust from zones C1, C2
=ESS.TS.ISS.G01.G03 1134 Outlet of exhaust gases (from Transport hall)
=ESS.TS.ISS.G01.G04 1135 Air supply for zones C3 (Utility)
=ESS.TS.ISS.G01.G05 1136 Air exhaust from zone C3
=ESS.TS.ISS.G01.G06 1137 Air exhaust from zone C4 (Active Cell)
Water circuits:
=ESS.TS.ISS.G01.W01 1138 Hydraulic system for TS HVAC - Hot water system feeding AHUs
=ESS.TS.ISS.G01.W02 1138 Hydraulic system for TS HVAC - Hot water system feeding FCs
=ESS.TS.ISS.G01.W03 1138 Hydraulic system for TS HVAC - Heat recovery system
=ESS.TS.ISS.G01.W04 1139 Hydraulic system for TS HVAC - Cooling water system feeding AHUs
=ESS.TS.ISS.G01.W05 1139 Hydraulic system for TS HVAC - Cooling water system feeding FCs

## Slide 9: Ventilation systems (C1, C2 classes)
dedicated to High Bay, Transport Hall, Personal Access Block, Technical Galleries and Active Cell Facility (only supply air)
two redundant air handling units control the temperature of the air supplied to the premises through galvanized steel air ducts
air heaters and coolers cover higher local loads
two reduntant exhaust fans extract air from the premises through the ductwork from painted carbon steel
single stage HEPA filter assemblies
discharge outside through the stack
=ESS.TS.ISS.G01.G01 and =ESS.TS.ISS.G01.G02

## Slide 10: Ventilation systems (C3, C4 classes)
=ESS.TS.ISS.G01.G04, =ESS.TS.ISS.G01.G05 and =ESS.TS.ISS.G01.G06
dedicated to Utility Block and Active Cell Facility (only exhaust air)
two redundant air handling units control the temperature of the air supplied to the premises through galvanized steel air ducts
air coolers distributed the Utility Block cover higher local loads
two reduntant exhaust fans extract air from the premises through the ductwork from painted carbon and stainless steel
two stages of HEPA filter assemblies
discharge outside through the stack

## Slide 11: Main components
4 air handling units (2 working and 2 redundant)
7 exhaust fans (4 working and 3 redundant)
13 HEPA filters stations (63 filter cassets in total)
over 100 dampers both motorized and manual
9 local air heating units, 3 electrical radiators
galvinized, carbon steel painted and stainless steel ductwork
heating and cooling water distribution pipework
propylene glycol heat recovery loop
Target HVAC

## Slide 12: TS HVAC technical rooms
Accelerator to Target (A2T) area

## Slide 13: A2T level 125
exhaust fans
HEPA filter stations
heat exchanges
exhaust ductwork connection to the stack
HVAC Technical room D02.125.4014

## Slide 14: A2T level 150
air handling units
pumps
control cabinets
HVAC technical room D02.150.4015

## Slide 15: Commisioning status
Target HVAC system performance test is ongoing on the site at the moment with the participation of IK partner from Chezh Republic

## Slide 16: System ballancing challenges
Performed measurements using Pitot static tube method according to SS-EN 16211:2015 Ventilation for buildings - Measurement of air flows on site –Methods
Accessibility of the premises
Working outside of normal hours
Working ”off-hours”

## Slide 17: System balancing challenges
6 ventilation systems
Many of systems to put to work simultaneously

## Slide 18: System ballancing challenges
Blocked air ducts and balancing dampers by the installations from other systems
Accessibility of the equipment

## Slide 19: System balancing challenges
Air ducts are located on the height up to 12 m (it is planned to use a drone with camera to check the integrity of the air ducts during the operation)
Heigh of air ducts placement

## Slide 20: End of presentation Thank you for your attention Questions?