## Slide 1: Introduction to Oxygen Deficiency Hazard (ODH) Accelerator Division Retreat Duy Phan Accelerator Safety Engineer
November 12th
Oxygen Deficiency Hazard: any operation which may expose personnel to an increased risk due to oxygen deficiency

## Slide 2: Definition
In low enough oxygen concentrations the first physiological symptoms of a problem can be unconsciousness, coma and death.
Two factors make ODH so dangerous...
The large volume ratio between a cryogenic liquid and its gaseous state at room temperature and pressure.
1
2
Oxygen Deficiency Hazard (ODH) is caused due to oxygen displacement

## Slide 3: ESS’ Cryogenic inventory
Accelerator tunnel
High-β: 21 x 0,192 m3 LHe
Medium-β: 9 x 0,184 m3 LHe
Spoke: 13 x 0,120 m3 LHe
ACCP
Gas storage
TICP & TMCP
Compressor Bldg.
TMCP: 2 x 63,5 m3 GHe
TICP: 1 x 64 m3 GHe
ACCP: 16 x 63,5 m3 GHe
HP: 3 x 20 m3 GHe
LN2: 2 x 20 m3
Cold Box Hall
Dewar ACCP: 20 m3 Lhe
Dewar TICP: 5 m3 Lhe
Cold Box: negligible
Test stand
Cold Box Hall
Acknowledgement : N.GAZIS, X.WANG, P.ARNOLD, W.HEES (ESS)
But also…
Target moderator
Science labs.
Elliptical
Spoke
4th largest Helium inventory in Europe

## Slide 4: Example
20 kg TNT equivalent
Atmosphere = 21 % O2
Liquid Helium (LHe)
Pressure: 1.3 bars
Volume: 1 m3
Temperature: 4.5 K
Helium Gas (GHe)
132.65 m3 !!
Volume of the room = 175 m3
5 % O2
P
Mount Everest
8840 m
The time between a failure and explosion may take a fraction of a second, eliminating warning signals as compensatory measures

## Slide 5: Example of LHe spill at CERN (2014)
Acknowledgement : G.LINDELL (CERN)

## Slide 6: ESS Safety Policy on ODH
ESS has defined 18% O2 as the safety threshold under which control measures shall be implemented
WHY?
1
Lessons learnt from similar Accelerator Facilities (e.g. CERN, FERMILAB)
2
Comply with the Work Environment Legislation
3
Prevent health effects

## Slide 7: Health Effects from O2 depletion
Acknowledgement : FESHM Chapter 4240 – oxygen deficiency hazards (odh) (fermilab)
Previous example
ESS Threshold

## Slide 8: ODH Control Measures
How do we plan to mitigate ODH ESS wide?
Warning signs
Ventilation
Oxygen monitoring (fixed)
+ alarm
Training
Personal oxygen monitor
Procedures
Self-rescue mask
And what about CERN…?

## Slide 9: CERN self-rescue mask
Acknowledgement : M.VIGUIER (CERN)

## Slide 10: ODH in the Accelerator Tunnel
Proton beam
Fire damper
Air supply
Air exhaust
O2
O2
O2 detector
O2
O2
O2
ODH is not relevant during beam operation
Preliminary design

## Slide 11: ODH in the Accelerator Tunnel
Failure scenarios (during access)
Scenario
Rupture of the power coupler’s window or beam line
Discharge of GHe through the 2 rupture disks located on the LHe line (2 s)
Max. mass flow rate = 15,2 kg/s
Loss of the content of 1 High-Beta cryomodule (28,4 kg at 2 K and 2.04 bara)
Acknowledgement : C.DARVE (ESS), J-P.THERMEAU (IPNO)

## Slide 12: ODH in the Accelerator Tunnel
Air supply
Air exhaust
25 200 m3/h
25 200 m3/h
If a Helium discharge occurs, it will be partly handled by the ventilation system…
≈140 hours of maintenance/year
O2
O2
O2
O2
O2
O2
O2
O2
But will it be sufficient to ensure a safe evacuation of the workers?

## Slide 13: Computational Fluid Dynamics (CFD)
Acknowledgement : N.GAZIS (ESS)
219 m to the last cryomodule
51 m to the nearest exit
64 seconds (30+34) to reach the nearest exit

## Slide 14: Computational Fluid Dynamics (CFD)
Near the faulty cryomodule
Acknowledgement : E.LUNDH (ESS)
ESS Threshold
Accesible area
Accesible area

## Slide 15: Computational Fluid Dynamics (CFD)
At the A2T area
Acknowledgement : E.LUNDH (ESS)
64 seconds (30+34) to reach the nearest exit
ESS Threshold

## Slide 16: Questions
Any Questions
Contact: duy.phan@esss.se
?