## Slide 1: ESS ICS Hardware choices
Timo Korhonen
ICS Chief Engineer
www.europeanspallationsource.se
2016-04

## Slide 2: Outline
Control System Hardware strategy – recap
PLC
EtherCAT
MTCA
  Platform issues
  Digital Frontend Platform
Advantages, risks, status
Summary
Signal speed
10 Hz
1 Hz
0.1 Hz
100 Hz
1 kHz
10 kHz
100 kHz
1 MHz
10 MHz
Electronic front-end platform
EtherCAT
Industrial automation (PLC)

## Slide 3: Hardware strategy – recap (from TAC 10)
Control systems have a lot of interfaces
  Need to cater for a spectrum of I/O requirements
    Fast, real-time signal processing
      State-of-the-art technology, evolving fast
      FPGA-based processing
      MHz to GHz range of signal acquisition
    Middle-range I/O
      Requires synchronization, kHz range I/O
    Non-real time industrial I/O
      Typically PLC-based
    Off-the-shelf devices
      Serial, Ethernet or other fieldbus devices
No single platform can cover this cost-efficiently!

## Slide 4: PLC
With a (tendered) framework agreement, Siemens S7-1500 has been selected as the ESS standard PLC
Documentation and a list of standard modules available in Confluence (https://ess-ics.atlassian.net/wiki/display/HAR/PLC)
EPICS integration with “soft” virtual IOCs, or if the application requires, with an industrial PC.

## Slide 5: EtherCAT
      For applications that “Require synchronization, kHz range I/O”
      Two-prong strategy
        Open source EtherCAT master for general I/O and simple (single-axis) motion control applications
          Simpler system, no extra PLC
        Beckhoff PLC & separate IOC for motion control with demanding requirements (e.g., multi-axis coordination) and I/O
      Development of an FMC EtherCAT slave module in-kind with Estonia
        Bind together EtherCAT and MTCA, or FPGA-based mini-IO
          transport time stamps to EtherCAT motion control directly from timing system
        Beam data to EtherCAT
        EtherCAT data to MTCA system

## Slide 6: MTCA – as a platform
Working on MTCA standardization for ESS
  Crate, power supply, MCH
  Goals: Cost, Reliability, Availability, Maintainability
MTCA.4 issues
  Long-term future of the platform is a concern
    e.g. SLAC decided to abandon it after several years of development
  Selection of available components and solutions is too small
  Market share is limited to very few players in the research market (which is small to begin with)
  Interoperability continues to be an issue
    If the market does not grow, it is questionable if this will ever be solved

## Slide 7: MTCA – as a platform (#2)
Why, what & how of MTCA standardization
  Why #1:Facilitate installation & system commissioning
    Minimize interoperability issues: main headache with MTCA.4
    Increase availability (fighting with troubleshooting costs time)
  Why #2: Ensure maintainability
    ICS has to manage the whole infrastructure in operation
  What: Learn, specify & standardize
    Crates, power supplies, fan units, MCH
  How: Collect information and study
    Learn what others have done
    Buy components for testing, talk to manufacturers, request fix if not OK
      Off-the-shelf is often not sufficient!

## Slide 8: Status of MTCA standardization
Some information collected
  https://ess-ics.atlassian.net/wiki/display/HAR/MTCA.4+COMPONENTS+EVALUATION
Hardware procured for testing
  Deliveries and repairs can take a long time!
Lab testing to be started
  Not yet systematically done, some initial effort spent

## Slide 9: MTCA processing and I/O
Common Digital Platform
  A board for MTCA.4 that can host almost all applications that need FPGAs, high throughput and/or fast real-time responses
In-kind effort with PSI & commercial partner
  IOxOS SA in Gland, Switzerland
  Based on an existing architecture

## Slide 10: Common Digital Platform
Architecture
  Combination of a FPGA with a CPU, connected with PCIe
    I/O primarily via FMCs (VITA 57.1)
    FMCs allow reuse of digital platform for several purposes
  CPU allows for
    Flexibility in programming (cf. Xilinx SDSoC concept)
    Scalability: Instantiate similar simple resources instead of building a single complicated one
  PCI express
    Is the most common computer interfacing standard today
      Also the basis of MTCA.4
    More complicated than e.g. UDP but provides full feature set
      DMA, SR/MR-IOV, interrupts, etc.
    Requires more infrastructure handling (PCIe enumeration, NT port mapping, etc.)

## Slide 11: Common Digital Platform
Common Digital Platform Variants
  Pure FMC carrier
    Full flexibility and reusability of FMC infrastructure
  Variant for Analog I/O through Rear Transition Modules
    A lot of existing designs based on uRTM
    Substitute one FMC slot with ADCs on-board
    Full firmware compatibility
      Fixed ADCs follow FMC interfacing pattern
    Application-specific
      Limits the use of this variant to the specific cases that follow DESY Zone 3 A.1 standard (to be proposed for standardization in PICMG)

## Slide 12: Common Digital Platform
Advantages
  A lot of proven infrastructure available
  Full documentation and source code available for ESS, including in-kind contributors
  Can be tailored to ESS requirements
    that are only now becoming clear (e.g., MPS interfaces)
  Modular architecture allows for evolution
    FMCs can be introduced and replaced as needed
    Digital platform can be reused as well
    Infrastructure code can be ported to new generations
      Firm- and software plus integration represent the biggest value (or cost), reusability is very important
An addition to the MTCA.4 infrastructure
  New I/O and processing solutions
  Aims to add to the attractiveness of the platform

## Slide 13: Common Digital Platform
Risks
  Start of the project has been slow
    In-kind process start takes time
  MTCA.4 issues may appear
    Although the partners (IOxOS SA and PSI) have a lot of experience, this is the first real experience with MTCA.4
  Substantial in-house knowledge will be required
    Working on that…but this needs to be taken seriously
  MTCA.4 as a platform has its risks
    Need to find the right partners in order not to get stuck
    IPMI solutions, licensing, incompatible size variants,…
  Single source?
    Largely mitigated by availability of full documentation and data needed for production.

## Slide 14: Common Digital Platform
Status
  Start of the project has been slow
    In-kind process in general, priorities of the laboratories
  Technically in agreement of scope and deliverables
    Technical annex close to completion
    Preparatory work has been going on in the background
  Conceptual study done, with already a lot of detail
    a lot of experience with similar designs
    Variants add complexity to the project
      Technical risks limited but schedule and cost risks grow
      Special-purpose variant has a bigger obsolescence risk
  Preliminary target date for production-ready design
    End of 2016
    Time-critical, any further delays add to (multiple) project risks

## Slide 15: Summary
Three-layer strategy for controls hardware
  Was already presented in TAC #10
  Has been communicated to stakeholders
    In use at in-kind contributors, e.g. CEA Saclay
MTCA.4 developments ongoing
  Platform has its risks – yes, we know.
  Work to be done to develop robust standards
Common platform
  To maximize re-usability of firm- and software
  To provide a roadmap for future development
  To be an open (as far as possible) platform for all ESS stakeholders
  Is time-critical