## Slide 1: Target Station Heating Ventilation Air Conditioning System Bounding Event: Loss of Dynamic Confinement in the Active Cell
Per Nilsson, CFD specialist
Andrea Polato, WU Leader, TS HVAC
www.europeanspallationsource.se
6 april 2016

## Slide 2: Introduction

## Slide 3: Introduction
3
3

## Slide 4: Active Cell
4
4
Maintenance Cell
Process
Cell
From target dismantling operations:
Dusts + gases

AIRBORNE CONTAMINATION
Confinement of the contamination
Active Cell structure
Active Cell HVAC
SAFETY FUNCTION
OPERATIONAL GROUP

## Slide 5: Active Cell and Adjacent Rooms

## Slide 6: Accident Description

## Slide 7: Accident Description
7
Target dismantling ongoing
Active Cell HVAC OFF
Pressure inversion
Dose to operators

## Slide 8: Accident Probability

## Slide 9: Accident Probability
9
Postulated initiating events occurrence
Target wheel Dismantling operations occurrence
Every 5 years
For a total duration of 3 months
total

## Slide 10: Radiological inventory & Release fraction from the source

## Slide 11: Radiological Inventory
11
Airborne contamination
inside the Active Cell
Preliminary classification according to ISO 17873:
Release fraction from the source
8000 DAC
Design value for the Active Cell’s Leak rate:
9 m3/h
=
2.55x10-3 vol/h

## Slide 12: Radiological Inventory
12
DETAILED EVALUATIONS ONGOING
DETAILED EVALUATIONS OGOING
Airborne contamination
inside the Active Cell

## Slide 13: Unmitigated accident

## Slide 14: Unmitigated scenario
No detection of the HVAC stop
Worker stays in the control volume for half a shift
9000 m3
3300 m3

## Slide 15: Unmitigated scenario
Severity (mSv) Probability | 0-1 | 1-10 | 10-20 | 20 to ≤ 50 | 50-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
MITIGATION MEASURES NECESSARY

## Slide 16: Mitigated Accident

## Slide 17: Unmitigated scenario
Dynamic confinement monitor
Alarm signal
Evacuation procedures
Mitigation measure
Reduced control volume:
Control volume located next to the active cell wall;
Operator remaining in the control volume for the given time;
At the alarm reception worker leaves the space
Limited permanence of the operator in the areas

## Slide 18: Unmitigated scenario
Severity (mSv) Probability | 0-1 | 1-10 | 10-20 | 20 to ≤ 50 | 50-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
RISK MITIGATED

## Slide 19: Conclusions

## Slide 20: Conclusions
During normal operations the confinement of the contamination is ensured by:
Active Cell Structure
Active Cell HVAC
In case of HVAC stop (off normal operations) the and no mitigation are foreseen:
Consequences for operators are NOT ACCEPTABLE
Mitigation:
Monitoring ( example: differential pressure monitor)
alarm
evacuation procedures
Limit to the exposure time  limit to the dose received
Consequences for operators are ACCEPTABLE
Operational Group
Safety Group