## Slide 1: MyRestore
Jlab’s Archiver-based Save, Restore & Compare System
Theo Larrieu
Analysis & High Level Applications Group
Jefferson Lab

## Slide 2: Outline
Introduction
Implementation
  Components
  Process
Usage
  Restore & Compare
  “Saves”
  Auto Restore
Restore Procedures
  Overview
  Examples
Status

## Slide 3: Introduction - Features & Benefits
Centralizes saving PV values in the archiver
  Eliminated redundant infrastructure to create and manage PVs in BURT files
Preserves all value changes
  Allows restore to an arbitrary point in time.
Allows dynamic restore procedures
  Utilizing external data sources.(e.g. the CEBAF Element Database or IOC signal.list files)
Automatic restore following an IOC reboot
Not just for IOCs
  MyRestore also now backs machine configuration save & restore.

## Slide 4: MyRestore Components
Mya Archiver
  Archives PV history and provides Restore values.
MyRestore MySQL database
  Stores Restore Procedure Definitions
MyRestore Web Application
  Interface to the MyRestore MySQL Database
MyRestore & myRestoreGUI executables
  Performs Restore Procedure
iocBootSpy
  Performs Automatic IOC restoration

## Slide 5: Mya Archiver
MySQL-based archiver developed at JLAB
  In use since February 2007
Distributed Architecture
  Currently Six (+1) hosts
Fallback archiver
  All channels, 30 days history.
236,368 channels archived
~20,000 updates / second received
7,223 updates / second stored (dead bands)
  ~16GB/day
Can stream ~300,000 history updates / second to clients
~2 years of channel history currently available online.
  Soon all data since 2008

## Slide 6: Web Server
Primary Interface to the MyRestore MySQL Database.
Allows users to view, create, edit Restore Procedures, Saves, and Data Source rules.
Exposes data to the myRestore command tools line via REST API

## Slide 7: MyRestore Process
Client contacts the MyRestore web server to obtain Restore Procedure definition.
Client obtains values for each PV named in retrieved Restore Procedure from Mya Archiver.
Client writes the PV values to the IOC via Channel Access.
Client makes a logbook entry.
Notes: Should rework the graphic to flip steps 1 and 3

## Slide 8: Usage
The primary tool for using MyRestore is the myRestore executable.
myRestore capabilities include
  Execute a Restore Procedure
  Validate a Restore Procedure
  Compare Historic vs. Current Values for PVs in a Restore Procedure
  Create a BURT req file or snap file

## Slide 9: IOC Restore Examples
Simple Case (Auto Timestamp)
  myRestore –ioc –R ${IOC}
Specify Relative Timestamp
  myRestore –ioc –R ${IOC} –t -1h
Specify Absolute Timestamp
  myRestore –ioc –R ${IOC} –t “2016-04-30 16:00”
Strict Mode (abort on first failure)
  myRestore –ioc –R ${IOC} –s
See All Options
    myRestore –h ioc

## Slide 10: About IOC Auto Timestamp
MyRestore queries Mya to find the most recent IOC disconnect time that was preceded by a "needs restored" transitioning to "NO“ where the time between those events was greater than 5 minutes.
Chooses the time 4 minutes before that IOC disconnect.
User can ask myRestore what timestamp it would choose:
  myRestore –stamp –i ${IOC}
Needs Restore
Restored
Needs Restore
Disconnect
5+ minutes
4 minutes
Time
*
Notes: In other words, finds the must recent disconnect time following at least 5 minutes of restored uptime.

## Slide 11: Restore Set Validation
Checks:
  PVs are being archived
  PVs exist in EPICS
  Executable paths exist and are executable
% myRestore -validate -R iocnl22rffcc1 -v
iocnl22rffcc1
Rf12Fcc
Pause step ok
Execution step ok
c100_rffcc: PVs:32 Errors:0 Warnings:0
Execution step ok
Execution step ok
Execution step ok
system: PVs:3 Errors:0 Warnings:0

## Slide 12: Restore Set Comparison
Report on differences between current values and historic values at arbitrary timestamp.
% myRestore -compare -R iocnl22rffcc1 -t -90d -v
c100_rffcc (32):
R1M1TDOFF: 92.0709 -> 88.4729
R1M1RATN: 14.8889 -> 13.6111
R1M1PSifpw: 106.5 -> 59.7382
R1M1PSET: -22 -> -55.738
R1M1POFF: -124.81 -> -41.5979
R1M1GSET: 18.3 -> 17.4824
R1M1GLOS: 1.39072 -> 0.869257
R1M1DACMUX: 1024 -> 1027
R1M1CNTL1b: 4 -> 0
R1M1CNTL1: 4 -> 0
system (3):

## Slide 13: IocBootSpy
Daemon process running on Linux.
Triggered by monitored <ioc>::ioc_sr.VALD connecting and being '1'.
Calls myRestore command line app to perform restore operation.
Executes in “strict” mode.

## Slide 14: IOC “Saves”
A save is simply a named, annotated timestamp.
Largely unnecessary for IOCs, but available
Saves are versioned.
  Repeated saves to the same name increment the version counter
    iocnl22rffcc1-1
    iocnl22rffcc1-2
  When used in a restore context
    Omit the version suffix to mean most recent version
    Include the version suffix to specify a specific version
Saves can be made retroactively
  Just specify the date & time instead of assuming now

## Slide 15: Restore Procedures
PV Sets
  Lists of PVs to restore (think BURT req files)
  May require macro variables to be fulfilled at runtime
  May reference data sources
Restore Sets
  Multi-step restore procedures consisting of
    PV Sets
    Unix programs or scripts
    Pauses
    Prompts (not valid for auto-restore)
    Nested Restore Sets
  Supply values for macro variables required by the included steps

## Slide 16: Restore Procedure - Static PV Set Example
BURT Req File “Cut-and-Paste”

## Slide 17: Restore Procedure– Variable Substitution Example

## Slide 18: Restore Procedure – Multi-step Restore Set
Three different step types used here:
  Executable (burtwb writes snap file with constants)
  Pauses
  PVSets
Intended for inclusion by another Restore Set that will provide values for the macro variables $(REBOOTPATH), $(IOC), $(BLDGNUM), $(ZONE)
Does provides a value for one required macro variable $(REBOOTPATH)

## Slide 19: Restore Procedure – Data Source Example

## Slide 20: About Data Sources
Simple Specification
  A Class with a getData() method that returns an array of strings.
Three different interfaces currently available
  CEBAF Element Database (CED)
  JData ( JLAB On-the-fly EDM screen generator data sources)
  signal.list (Regular expressions extract strings)
Nightly Report informs Mya Administrator if data source changes require new PVs to be archived.

## Slide 21: Restore Procedure – non-IOC Example
The Accelerator “Allsave” Master used to save and restore machine configuration is defined as a hierarchical Restore Procedure.

## Slide 22: Current Status
Implemented on 210 (53%) of the 397 IOCs that are “Production/Available/OPS”
  Primarily IOCs of the Magnet, RF, and SEE BPM systems.
  Goal: Convert remainder during 2016 Summer Shutdown.
Has recorded 1426 successful restores to the electronic logbooks since August 2015.

## Slide 23: The End
Thank you for your attention

## Slide 24
Begin Extra Slides

## Slide 25: Steps to Create an IOC Restore Set
Identify the apps on the IOC.
Create a new IOC Restore Set.
Add Restore Steps for each app.
Ensure values for all required macro variables.
Validate the Restore Set
Request that archiving begin.
Register the IOC in CED as MyRestore or MyRestoreAuto
Perform a test restore and/or reboot

## Slide 26: Step 1 - Identify Apps on the IOC
  For legacy IOCs one can examine
  /cs/opshome/burt/REBOOT/scripts/src/switch.OPS
% more Switch.OPS
# Begin OPS IOCs
# NOTE - be sure system application is last in the kindofs statement
case 313:
set kindofs = (system)
# set kindofs = (bunch fsd camacVer system)
breaksw
case 313a:
set kindofs = (system)
breaksw
case bcm:
set kindofs = (bcmVme system)
breaksw
case bd1:
set kindofs = ()
breaksw
case bpmhap1:
set kindofs = (HappexBpm system)
breaksw
case ea1:
set kindofs = (fsd bpm vac system)
breaksw
case ea1mag:
set kindofs = (magnet system)
breaksw
case ea2:
set kindofs = (fsd bpm blm vac system)
breaksw
case ea2mag:
set kindofs = (magnet system)
breaksw

## Slide 27: Step 2 - Create the IOC Restore Set
Option 1 – Clone from an existing similar IOC.
After cloning, the macro variable $(IOC) will automatically be updated to the new IOC name.
Option 2– Create a new Restore Set.
The “system” PV Set will automatically be linked to the new Restore Set.
The macro variable $(IOC) will automatically be assigned the IOC name as a variable.
Be sure to name the new Restore Procedure to match the IOC name!

## Slide 28: Step 3 - Add Restore Steps for each app
Restore Procedures named after the app they represent streamlines finding and adding them to the IOC.

## Slide 29: Step 4 – Ensure All Macro Variables have values
Here we can see values being provided for all three macro variables required by the steps in the prior section.
We can also see that the $(SLD) variable is being assigned multiple values.

## Slide 30: Step 5 – Validate the Restore Set
The only warnings you want to see in the validation report are PVs that are not archived.
Other errors should be fixed before proceeding.

## Slide 31: Step 6 – Request Archiving
If archiving has never been initiated for a Restore Set, there will be a button on its web page labeled “Request Archiving”. Pressing this will send a request to the Mya Administrator.

## Slide 32: Step 7 – Update CED
Set the ScreenSaveOption property:
  MyRestore - Tells OTF screens to invoke the myRestoreGUI from IOC screen(s).
  MyRestoreAuto – Also registers the IOC with iocBootSpy once merged to OPS.
Step 8 – Test
Perform a test restore on the IOC.
The testing should include rebooting the IOC, especially if MyRestoreAuto.

## Slide 33: CED Data Source
Ideal for keeping restore procedures in sync with CED
A stored CED query that returns a list of elements or a property thereof (Ex: EPICSName).
Transformations available
  Uppercase
  Lowercase
Exclude lists

## Slide 34: Signal.list Data Source
Use a regular expression to pull PVs from an IOC’s signal.list file.
Signal.list files are uploaded to myRestore database tables every night
  /cs/op/iocs/myrestoreSignals.sh

## Slide 35: JData Data Source
Permits the use of an available OTF JData data source to provide an element list.
Currently Available:
  Trims by IOC
  Shunts by IOC
  BPMs by IOC

## Slide 36: Dynamic PV Set Example
$(BPM) macro variable is declared
  Value(s) to be fulfilled at run time.
@(SEEMultiPassCrate) specifies a data source that will be used at run time.
Two PVs are prefixed with RO
  Will be archived
  Useful for comparisons
  Will not be written during restore.

## Slide 37: IOC Save Examples
Create with current timestamp and a description
  myRestore –save –n ${IOC} –d “my description”
Create an IOC Save for a specific (past) timestamp
  myRestore –save –n ${IOC} –t -1h –d “my description”
List saves for an IOC
  myRestore –save –n ${IOC}
% myRestore -list -saves -n "iocse17-*" -v |
iocse17-12 2016-04-25 08:58:50
DEFAULT
francis
saveIOCS
iocse17-11 2016-04-25 05:27:56
DEFAULT
higgins
saveIOCS
iocse17-10 2016-03-10 05:55:39
DEFAULT
francis
saveIOCS

## Slide 38: Restore Set Listing
List PVs
  -b for BURT Format
% myRestore -pvs -R iocnl22rffcc1 -b
# c100_rffcc
R1M1CNFGA
R1M1CNFGC
R1M1CNFGD
R1M1CNTL1
R1M1CNTL1b
List PVs with values
  -b for BURT Format
  -t timestamp for values
% myRestore -pvs -R iocnl22rffcc1 -b -t -1d
--- Start Burt header
Time: Mon May 2 15:12:00 2016
Login ID: theo (Theodore Larrieu,,,)
Eff UID: 4280
Group ID: 106
Keywords:
Comments:
Type: Absolute
App: myRestore 2.6.1
Req File: c100_rffcc
--- End Burt header
R1M1CNFGA 1 0
R1M1CNFGC 1 0
R1M1CNFGD 1 0
R1M1CNTL1 1 4