## Slide 1: Introduction to Pilot TSS
Linda R. Coney
Group Leader – Target Safety and Controls
www.europeanspallationsource.se
February 15-16, 2016

## Slide 2: Outline
TSS purpose and scope
Target Radiation Safety Hazard Analysis
TSS g Pilot TSS
Pilot TSS Concept
Conclusions

## Slide 3: TSS – Purpose
The Target Safety System (TSS) is a safety classified, active monitoring and control system that shall:
  Protect workers and public from exposure to unsafe levels of radiation and prevent the release of radioactive material beyond permissible limits
  Bring the target station into a safe state in case of an abnormal event from the nuclear safety point of view

## Slide 4: TSS Scope
Where does TSS fit within overall Target Safety Strategy?
Target Station Safety
Radiation Safety
  Ionizing radiation
  Activation
  Contamination
Conventional Safety
  High voltage
  Chemical hazard
  ODH
  Cryogenics
  Working at heights, ….
TSS
4
TSS is only involved with Radiation Safety
TSS is part of the Radiation Safety strategy

## Slide 5: TSS Scope
Concerned with release of radioactive material
  Tied to monitoring of system parameters – it is not an access control system
Requirements are based on the radiation safety hazard analysis evaluation for Target systems
  Includes monolith & supporting systems, Active Cells, beam dump
  Includes accelerator and instruments only to the extent that they jeopardize inventory in the Target station
    Proton beam as aggressor to target wheel, Chopper failure as aggressor to monolith
Target Station Radiation Safety Hazard Analysis
Events/Accidents
  H2 – H5
Normal Operations
  All modes including beam to dump, beam to target, maintenance mode
TSS

## Slide 6: Target Radiation Safety Hazard Analysis: Dose Limits
ESS GSO FROM SSM |  | 
ESS Safety Objectives |  | 
Operating conditions Initiating event likelihood | Workers limit (effective dose) | Public limit (effective dose)
Normal operation - H1 | 10 mSv/year | 0,1 mSv/year
Incidents – H2 | 20 mSv/event | 0,1 mSv/event
Unexpected events – H3 | 50 mSv/event | 1 mSv/event
Design Basis Accident – H4 | 50 mSv/event | 20 mSv/event
Highly improbable events – H5 Ex : plane crashes, major earthquake |  | 100 mSv/event
6
Protect workers and public from unsafe levels of radiation
Prevent the release of radioactive material beyond permissible levels
Defining consequence = dose to public and workers
  These limits have been set by SSM (public) and ESS (workers)

## Slide 7: Target Radiation Safety Hazard Analysis: Severity Matrices
H1 shaded out – indicates normal operation – limits per year
  Normal operation limits and releases are handled separately from this analysis
H2 – H5 dose limits are per event
Limits for Public set by SSM
Limits for Workers set by ESS GSO (General Safety Objectives) except for H5 limit which we chose to equal that of the public because there was no limit stated
Severity (mSv) Probability | < 0.01 | 0.01-0.1 | 0.1-1 | 1-20 | 20-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
Unacceptable
Tolerable
Acceptable
Public
Severity (mSv) Probability | 0-1 | 1-10 | 10-20 | 20-50 | 50-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
Workers

## Slide 8: TSS Context: Target Station Radiation Safety
Where does TSS fit within overall Target Radiation Safety Strategy?
  TSS is part of our set of tools
Outcome of Radiation Safety Hazard Analysis for Target Station systems includes:
  Identification of safety functions
  Identification of safety SSCs (structures, systems, and components) and safety-related SSCs
  Classification of SSCs
Chart: 
| System Design | Administrative controls | Zoning | PSS | TSS
Contributors to Radiation Safety | 8.2 | 2.5 | 1.4 | 2.2 | 1

## Slide 9: TSS Context: ESS Control Systems
TSS - Limit transfer of radioactive contamination to the public, workers, and environment
PSS - Suppress radiologic hazards by switching off the proton beam
  Control access to restricted areas during operations
MPS – Protect investment from damage due to beam losses and malfunctioning equipment
  Optimize integrated machine performance
  Stop beam – Beam Interlock System
TSS – Independent safety-qualified system
g Not tied into other ICS systems
Personnel Safety System

## Slide 10: TSS Development
Qualitative Hazard
Analysis
Accident Analysis
Dose Consequence
Identify Safety Functions
Allocate Safety Functions to TSS
Requirements for TSS
Design TSS
Process ongoing for the Target systems and TSS
Ideally sequential
End result
  All safety functions identified
  SSCs designed including complete TSS as part of the comprehensive safety strategy for Target station
However – Hazard Analysis is complex and time consuming

## Slide 11: TSS g Pilot TSS
Assume:
Dose Consequence
Safety Functions
Allocate SaFs to Pilot TSS
Requirements for Pilot TSS
Design Pilot TSS
Select Accident Scenario
HA
Merge to Create Complete TSS
Hazard
Analysis
Other Accident Analyses
Dose Consequence
Identify Safety Functions
Allocate SaFs to TSS
Requirements for TSS
Design TSS
Decision was made to move forward with the TSS design
Design Pilot TSS
  Select accident scenarios from target wheel and helium cooling analysis
  Until completion of Accident Analyses, the possibility remains that requirements on TSS will change
Awaiting completion of HA

## Slide 12: Pilot TSS Concept
Goals
  Target Station shall operate safely, reliably, and with high availability
    No mandate to maintain facility availability upon action by Pilot TSS
  Target Station shall protect workers and the public from radiation exposure beyond allowable limits
  Radioactive releases to the surrounding environment shall be prevented or, if this is not possible, controlled and mitigated
  Pilot TSS shall bring the target into safe state in case of an abnormal event from nuclear radiation safety point of view
    Defined as no beam on target for Pilot TSS accident scenarios

## Slide 13: Pilot TSS Concept
Assume:
Dose Consequence
Identify Safety Functions
Allocate SaFs to Pilot TSS
Requirements for Pilot TSS
Design Pilot TSS
Select Accident Scenario
Assume Pilot TSS needs to:
  Detect stopped wheel rotation
  Detect loss of target He cooling
  Shut down proton beam under these conditions
Define Pilot TSS safety functions (SaF)
  Assume dose and identify severity – determine SaF classification & requirements for design
Design complete Pilot-TSS system to fulfil safety functions
  Detection g decision g action (Logic, voting)
  Trigger mechanisms, sensors, PLCs, actuators
  Interfaces – Accelerator, Site Infrastructure, target wheel, PCool, ICS
  Evaluate reliability, FMECA
Pilot TSS
TSS

## Slide 14: Pilot TSS Concept
Architecture
  Standalone active safety credited control and monitoring system
    No dependency to other communication or control systems
    Utilize its own dedicated sensors and actuators to bring target monolith to a safe state w/o relying on any external system
  Includes physical separation, diversity and fail-safe criteria to such an extent that it can resist hazards that could impact Pilot TSS reliability
Interfaces
  Target systems – monitor and evaluate process variables continuously, any sign of failure causes action to go to safe state
  Accelerator – extract information related to operational modes to meet operational requirements
  MCR – status available for monitoring to operations personnel

## Slide 15: Pilot TSS Concept
Development standard
  Pilot TSS will follow international standard IEC61511
    Addresses safety-instrumented systems
    Electrical/electronic/programmable electronic technology
    Lifecycle and pragmatic quantification of risks and architecture provides valuable framework for safety engineering
    Applies to all possible risks
  Applying IEC61511 on systems-of-systems level and IEC61508 on the subsystem or components level
Licensing
  Pilot TSS is important part of licensing process for the ESS
  Subject to SSM conditions and legislations
  Subject to local rules concerning risk and hazard management as defined by ES&H

## Slide 16: Pilot PDR Presentations
Concept
ESS-0037596
Hazard analysis results overview
ESS-0050077
System requirements
ESS-0002776
Functions
ESS-0043617
ICD-R:s
ESS-0016380
ESS-0022915
ESS-0030063
ESS-0030068
ESS-0042356
ESS-0048755
Life-cycle process
SW design
ESS-00xxxxx
FMECA
ESS-0047128
He cooling variables ESS-0049507
Verification, commissioning and validation
ESS-0048372
Architecture & HW design
ESS-0045067
Hazard analysis process
ESS-0041755
Identified safety controls ESS-0050185
Accidents reports ESS-0040075
ESS-0044348
ESS-0050081
Standard selection
ESS-0047208
ESS classification
ESS-0016468
TSS Document Map
Jan Espen
Per
Monika
Mikael
Atefeh
Reliability Analysis

## Slide 17: Conclusions
Pilot TSS is part of the overall Target Radiation Safety Strategy
  Active control and monitoring system to protect the public and workers from release of radioactive material
  Detect stopped wheel
  Detect loss of target He cooling
  Shut down power to proton beam under these conditions
Pilot TSS developed to enable design of TSS in parallel with continuation of Target Radiation Hazard Analysis
  Follow IEC61511 lifecycle
  Includes logic, sensors, PLC, actuators, interfaces
  Analysis of reliability and failure modes
Much more information given in the rest of the PDR presentations

## Slide 19: Target Radiation Safety Hazard Analysis: Severity Matrix – Public
H1 shaded out – indicates normal operation
  Dose limits are per year
  Normal operation limits and releases are handled separately from this analysis
H2 – H5 dose limits are per event
Limits set by SSM
Severity (mSv) Probability | < 0.01 | 0.01-0.1 | 0.1-1 | 1-20 | 20-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
Unacceptable
Tolerable
Acceptable
Public

## Slide 20: Target Radiation Safety Hazard Analysis: Severity Matrix – Workers
Severity (mSv) Probability | 0-1 | 1-10 | 10-20 | 20-50 | 50-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
H1 shaded out – indicates normal operation – limits per year
  Normal operation limits and releases are handled separately from this analysis
H2 – H5 dose limits are per event
Limits set by ESS GSO (General Safety Objectives) except for H5 limit which we chose to equal that of the public because there was no limit stated
Unacceptable
Tolerable
Acceptable
Workers

## Slide 21: Target Station Radiation Safety Process
Based on
standards
ESS Classification Rules
Accident Analyses
Qualitative Hazard Analysis
Systems/ Components
Safety Function
Actions: (QA, Procedures) Analysis
Materials Manufacturing Installation
Inspection Testing
etc
Risks - Events
Safety
Class
Code
Class
Design/define the systems and context
Define (enveloping) events and frequency (H1-H5 probability)
Determine and categorize safety functions to prevent events (SaF)
Event Consequences
Calculate dose consequences of events (H1-H5 criteria)
Determine safety classification of equipment (SIC)
Choose classification in standards within the discipline