## Slide 1: Pilot TSS system requirements
Mikael Olsson
Control engineer – Target control
www.europeanspallationsource.se
15 February 2016

## Slide 2: ESS-0002776
Concept
ESS-0037596
Hazard analysis results overview
ESS-0050077
System requirements
ESS-0002776
Functions
ESS-0043617
ICD-R:s
ESS-0016380
ESS-0022915
ESS-0030063
ESS-0030068
ESS-0042356
ESS-0048755
Life-cycle process
SW design
ESS-00xxxxx
FMECA
ESS-0047128
He cooling variables ESS-0049507
Verification, commissioning and validation
ESS-0048372
Architecture & HW design
ESS-0045067
Hazard analysis process
ESS-0041755
Identified safety controls ESS-0050185
Accidents reports ESS-0040075
ESS-0044348
ESS-0050081
Standard selection
ESS-0047208
ESS classification
ESS-0016468

## Slide 3: Outline
ES&H requirements
ESS requirements
Hazard analysis / accident scenarios
TSS overall safety function
TSS safety instrumented functions
TSS system requirements
TSS function specification
ESS classification

## Slide 4: Top requirements - ESS
Extra: accelerator shall be allowed to produce and send proton beam to beam dump – even if target is not ready for beam Rationale:
  commissioning and maintenance of accelerator
  high availability of accelerator

## Slide 5: Top requirements –ES&H
Keywords
Prevention of events leading to radioactive releases
Usage of safety classes
Usage of “safe state”
Consider events up to and including event class H4
Resistance to malfunction
Single failures
Common cause failures
Design principles
Redundancy, diversity, physical separation

## Slide 6: Accidents

## Slide 7: ESS classification – need for safety function
Severity (mSv) Probability | < 0.01 | 0.01-0.1 | 0.1-1 | 1-20 | 20-100 | >100
H1 |  |  |  |  |  | 
H2 |  |  |  |  |  | 
H3 |  |  |  |  |  | 
H4 |  |  |  |  |  | 
H5 |  |  |  |  |  | 
C1
C1
C1
C1
C1
C1
C1
C2
C2
C3

## Slide 8: ESS classification – impact on TSS
“Proposal”

## Slide 9: ESS classification - identification of TSS
“Main radiation safety function”
“Detailed radiation safety function”
“Further detailed radiation safety function”
TSS is identified as one of ESS safety functions

## Slide 10: Overall safety function
Overall safety function | Normal operation | Req ID
TSS shall prevent target wheel tungsten temperature from exceeding 700 °C | 390 °C | TSS-TSS-100
Based on common hazard from AA1, AA3 and AA4 (likely TSS related consequences)
If >700 °C oxidation of tungsten becomes possible and more isotopes are released

## Slide 11: Instrumentation of overall safety function
Process variable Accident | Outlet velocity | Outlet pressure | Inlet temperature | Target shaft rotational speed
Target Wheel stop during beam on target - AA1 |  |  |  | X
Loss of He cooling flow (blower fail) - AA3 | X |  |  | 
Loss of He cooling pressure (leakage) – AA4 |  | X |  | 
Loss of He cooling heat exchange – AA3 |  |  | X | 
TSS cannot measure tungsten temperature due to high radiation level inside monolith
Instead monitoring tungsten cooling conditions
4 process variables identified

## Slide 12: Safety instrumented functions
Safety instrumented functions | Normal operation | Req ID
TSS shall prevent proton beam from reaching target if… |  | 
target He outlet velocity is < 35 m/s within 35 sec | 61 m/s | TSS-TSS-101
target He outlet pressure < 6.2 bar within 35 sec | 10 bar | TSS-TSS-102
target He inlet temperature > 230 °C within 35 sec | 40 °C | TSS-TSS-103
target shaft rotational speed < 11.6 rpm within 210 ms | 23.3 rpm | TSS-TSS-104
Target wheel stops instantaneously. 4:th pulse on same sector gives >700 °C.
Within 3 pulses after stop = 3*70 ms = 210 ms

## Slide 13: Target wheel stops – time constraint
p+1
p+2
p+3
p+4
Scenario | Tungsten T [°C] | Time [ms]
p+1 hits sector | 390 -> 490 | 
Rotation stops |  | 0
p+2 hits same sector | 590 | 70
p+3 hits same sector | 690 | 140
p+4 hits same sector | 790 | 210
X

## Slide 14: Safety system – overall function – instrumented functions

## Slide 15: System requirements
Requirement content (extracted from 61511)
Safe state
Modes of operation
Start-up and restart
System input and output
Manual shutdown
Failure modes and responses
Common cause failures
Single failures
Max allowable spurious rate
Operator interfaces
Proof test interval
Mean time to repair
Security
Environmental design for equipment
Tools for periodic test and replacement
Demand rate

## Slide 16: System requirements - examples

## Slide 17: IEC 61511 and SIL
Identified during hazard analysis
Probability for demand of TSS
Risk level including TSS
Safety classified design, passive safety functions etc.
TSS reliability = probability of failure on demand
SIL

## Slide 18: ESS-0043617
Concept
ESS-0037596
Hazard analysis results overview
ESS-0050077
System requirements
ESS-0002776
Functions
ESS-0043617
ICD-R:s
ESS-0016380
ESS-0022915
ESS-0030063
ESS-0030068
ESS-0042356
ESS-0048755
Life-cycle process
SW design
ESS-00xxxxx
FMECA
ESS-0047128
He cooling variables ESS-0049507
Verification, commissioning and validation
ESS-0048372
Architecture & HW design
ESS-0045067
Hazard analysis process
ESS-0041755
Identified safety controls ESS-0050185
Accidents reports ESS-0040075
ESS-0044348
ESS-0050081
Standard selection
ESS-0047208
ESS classification
ESS-0016468

## Slide 19: Functions
Function content (extracted from 61511)
Functional description
Primary action
Fail safe process input and output
Final elements
Trip limit and response time
Muting/bypass (beam to dump)
Activate/deactivate
Reset/restart
Spurious trips and reset failures
BPCS and other system interfaces
Proof test intervals
Protection from environmental conditions and accidents
Consequential hazards
Demand rate and safety integrity
HMI

## Slide 20: Conclusions
Requirement structure
ES&H interpretation of SSM requirements
Overall safety function based on likely accidents with assumptions (Pilot TSS)
  Prepared for changes (TSS)
Further details during detail design

## Slide 21
Break

## Slide 22: Design challenges
H2 events with consequences >20 mSv
  >20 mSv is only allowed for H5 events
  TSS to decrease probability H2 (>10-2) -> H5 (<10-6)
  Corresponds to <10-4 which is SIL4
  Layers of protection = count on process control and machine protection to decrease demand rate for TSS?
Target wheel stops instantaneously
  TSS must act within 210 ms (3 pulses) to prevent 700 °C
  Safety control equipment generally slow due to internal diagnostic functions
  Can target wheel stop within one sector?
  Is 700 °C the critical temperature?

## Slide 23: Questions
Who is defining requirements on TSS for single failure and common cause failures?
  SSM definitions
  ES&H interpretations/requirements
  Solution by SE (ESS classification - ESS-0016468)
Safe state - what is required to leave safe state?
  Due to spurious trip
  Due to real trip