## Slide 1: Pilot TSS architecture and hardware design
Mikael Olsson
Control engineer – Target control
www.europeanspallationsource.se
15 February 2016

## Slide 2: ESS-0045067
Concept
ESS-0037596
Hazard analysis results overview
ESS-0050077
System requirements
ESS-0002776
Functions
ESS-0043617
ICD-R:s
ESS-0016380
ESS-0022915
ESS-0030063
ESS-0030068
ESS-0042356
ESS-0048755
Life-cycle process
SW design
ESS-00xxxxx
FMECA
ESS-0047128
He cooling variables ESS-0049507
Verification, commissioning and validation
ESS-0048372
Architecture & HW design
ESS-0045067
Hazard analysis process
ESS-0041755
Identified safety controls ESS-0050185
Accidents reports ESS-0040075
ESS-0044348
ESS-0050081
Standard selection
ESS-0047208
ESS classification
ESS-0016468

## Slide 3: Outline
System and functions
Architecture and layout
Performance

## Slide 4
System and functions

## Slide 5: System and functions
Overall safety function
TSS shall achieve safe state if target wheel tungsten temperature > 700 °C
Safety instrumented functions
TSS shall prevent proton beam from reaching target if…
target He outlet velocity is < 35 m/s within 35 sec
target He outlet pressure < 6.2 bar within 35 sec
target He inlet temperature > 230 °C within 35 sec
target shaft rotational speed < 11.6 rpm within 210 ms

## Slide 6: Safety instrumented functions - inputs
Process variable Scenario | He outlet velocity | He outlet pressure | He inlet temperature | Target shaft rotational speed
Target Wheel stop during beam on target - AA1 |  |  |  | X
Loss of He cooling flow (blower fail) - AA3 | X |  |  | 
Loss of He cooling pressure (leakage) – AA4 |  | X |  | 
Loss of He cooling heat exchange – AA3 |  |  | X | 
SSZ
PSZ
TSZ

## Slide 7: Safety instrumented functions - output
Purpose = achieve safe state
Ion source
  Contactors stop allowing power to the Ion source
  Contactors dedicated to TSS
RFQ as a remaining potential redundant solution
Conventional electrical power (400 V)
High voltage isolation
High voltage electrical power generation
(75 kV)
Ion source high voltage area
Control
Coils
Magnetron
TSS control
Both closed = allow power
Any open = no power

## Slide 8: Safety instrumented functions - principal
Read
(sensors)
Target wheel He cooling outlet velocity
Target wheel He cooling outlet pressure
Target wheel He cooling inlet temperature
< 35 m/s
< 6.2 bar
> 230 °C
If inside all limits
Evaluate
(logic solvers)
Act
(final elements)
Close contactors at the ion source
If any limit exceeded
Open contactors at the ion source SAFE STATE
If sensor connection lost
If communication lost
If power lost
Target wheel shaft rotational speed
< 11.6 rpm
Diagnostic
If control HW failure
Fail safe

## Slide 9: Bending magnet impact
Requirement from accelerator:
  “accelerator shall be allowed to produce and send proton beam to beam dump – even if target is not ready for beam”
Solution
  Monitor bending magnets status
  If both bending magnets are grounded (beam to dump) -> allow beam

## Slide 10: System performance – bending magnet
Read
(sensors)
Target wheel He cooling outlet velocity
Target wheel He cooling outlet pressure
Target wheel He cooling inlet temperature
< 35 m/s
< 6.2 bar
> 230 °C
Evaluate
(logic solvers)
Act
(final elements)
Close contactors at the ion source
Open contactors at the ion source SAFE STATE
If sensor connection lost
If communication lost
If power lost
Target wheel shaft rotational speed
< 11.6 rpm
Diagnostic
If control HW failure
Fail safe
If beam to dump:
No evaluation of sensors
If inside all limits
If any limit exceeded
If beam to Target
If beam to Dump
No evaluation of sensors

## Slide 11
Architecture

## Slide 12: Architecture constraints
HW safety integrity (61511, SIL 3)
  Redundancy (single failure)
  Reliability
TSS is classified as C1
  Redundancy (single failure)
  Diversity (CCF)
  Physical separation (CCF)
Response time < 210 ms

## Slide 13: Architecture – overview

## Slide 14: Layout - overview
Common area for monitoring of process variables
Separate area for control equipment for the two trains
Common area for actuators to stop proton beam
Separate cable routes for the two trains
Common area for monitoring bending magnet status

## Slide 15: Sensors - architecture
Pressure sensors
TSS train 1
TSS train 2

## Slide 16: Sensor - alternatives
2 sensors (1oo2 voting)
(+) Less complexity
(+) Less configuration and maintenance
(-) Negative impact on availability
3 sensors (2oo3 voting)
(+) Increased availability by 2oo3 voting
(-) More complex
(-) More configuration and maintenance

## Slide 17: Logic solver - architecture
ET200SP station
Switch
Switch
Switch
F-PLC
ET200SP station
Sensors
Actuator 1
Actuator 2
F-Relay

## Slide 18: Logic solver – alternatives
PLC in both trains
(+) Less cables
(-) Hard to state diversity
PLC and relay
(+) Diversity for logic and cables
(+) meet advisory requests for relay solution
(-) more cables
Relay must be in TSS room #2 due to distance (max 1000 m)
Relay in both trains
(-) Hard to state diversity
(-) No option for diverse cables (fiber + copper)
(-) Long distance from TSS room #1 to FEB
(-) more cables

## Slide 19: Logic solver – relay alternatives
Simple relay (3SK1)
No SW configuration needed
(-) not flexible to expand
(-) response time increasing when expanding by adding relays
(-) less diagnostic
Middle relay (3SK2)
Minor SW configuration needed
(+) up to 20 inputs
(+) response time constant
(+) more diagnostic
(+) Built-in HMI (small, not configurable)
Advanced relay (MSS)
Minor SW configuration needed
(+) Can be further programmed = simple PLC
(+) up to 50 inputs
(-) More advanced than needed

## Slide 20: Final elements architecture
TSS train 1
TSS train 2
3-phase 400 V
Ion source

## Slide 21: Final elements – alternatives
Only ion source
(+) Safe, robust, simple
(+) Diversity by two different contactors
(-) Hard to resist CCF in case of external event (fire)
Ion source + RFQ
(+) Safe, robust, simple
(+) Diversity and physical separation
(+) Reduced effect by CCF in case of external event
(-) Potential damage of RFQ – might require delayed signal
More options
(-) slow

## Slide 22: Architecture ans components
PSZ
SSZ
Utility room
TSS room 1
TSS room 2
Front end building
x2
x2
x2
400 V
Ion source
TSZ
x2
ET200SP station
Switch
F-PLC
ET200SP station
HEBT (bending magnets)
ET200SP station
HMI
HMI
F-Relay

## Slide 23: Layout of components - ESS

## Slide 24: Cable routes - Target

## Slide 25: Cable routes - Target

## Slide 26: Cable routes - Target to FEB
Fiber cable
Outside and underground
Copper cable
Through klystron gallery

## Slide 27: Cable routes Target to FEB – alternatives
Accelerator tunnel
(+) accessible
(+) short distance
(-) radiated area
(-) not suitable for fiber cables
(-) area with a lot of maintenance
Klystron gallery
(+) non radiated areas
(+) short distance
(+) accessible
(-) area with a lot of maintenance
Outside underground
(+) non radiated areas
(+) suitable for fiber cable
(+) minor maintenance
(-) long distance
(-) not accessible

## Slide 28: FEB space allocation
Conventional electrical power (400 V )
High voltage isolation
High voltage electrical power generation
(75 kV)
Ion source high voltage area
Control
Coils
Magnetron
TSS control
p+

## Slide 29
Performance

## Slide 30: System performance - sensors
He velocity, pressure and temperature (switches)
Shaft rotational speed (pulse signal)
Gives immediate indication when process variable outside limit
P < 6.2 bar
v < 35 m/s Stop beam
T > 230 °C
10 V
0 V
Needs processing before decision if process variable outside limit
<--- Time consuming --->
Safe processing even more time consuming…
0 V
10 V
< 11.6 rpm -> Stop beam

## Slide 31: System performance - response time
 | TSS train 1 (Relay) | TSS train 2 (PLC) | Comment
Velocity, pressure and temperature | ~180 ms | < 200 ms | Contactor most critical
Rotational speed | ~270 ms | TBD | Process of pulsed signal most critical Speed monitoring F-relays are generally slow F-PLC cannot process pulsed signal Need extra components (relay, redundant “normal” PLC, etc)
Hard to achieve < 210 ms for shaft rotational speed
Contactors assumed 100 ms
+ ?

## Slide 32: Conclusions
Two train system – diverse and physically separated
Sensors and contactors shared by the two trains
Ion source
Difficult to fulfill 210 ms for rotational speed

## Slide 33
Thank you!

## Slide 34
If time allows…

## Slide 35: FMECA
Single failure OK
CCF
  Faulty manual setting of sensors limit (proof test required after sensor maintained)
  Faulty specification gives faulty behavior in both trains (project management to follow activities in 61511 to minimize this risk)
  External events (fire)
    Utility room: sensors damaged and locked in “OK” position
    FEB: contactors damaged and locked in “OK” position

## Slide 36: Challenges and questions
Challenges
  Safety instruments in radiated areas
  Response times (210 ms)
Questions
  Bending magnets monitoring only – or do we need to control?

## Slide 37: Extra