## Heading page
| Document Number | ESS-0020677
| Date | Mar 13, 2014
| Revision | 0 (1)
| State | Review
Classification
| Page | 1 (5)
Requirements validation plan
Target helium cooling systems
| Name | Title
Owner | Jens Harborn | Work unit leader - Target Helium Cooling
Reviewer | Ulf Oden | Lead Engineer - Target Systems
Approver | Eric Pitcher | Deputy head of Target division

## System verification plan
Requirements Validation plan; Target Helium Cooling |  |  |  | 2015.09.28
| Req. Id.nr | Requirement description | Note | Requirement verification
TOP LEVEL REQUIREMENTS ON TARGET COOLING SYSTEMS
STANDARDS - top level requirement
(according to Target station validation plan)
General requirements related to the Target Station applicable for the system
| PCool-001 | Reliability |  | Uptime log
| ICS-001 | Communication bus |  | Design review
Safety related requirements /GSO
| PCool-002 | Circuit shut-off valves |  | Design review
| PCool-003 | Radiation dose limits from components to people |  | Measurements
| PCool-004 | Heat exchangers barrier strength |  | Pressure/leakage test
| PCool-101 | Enclosure of helium |  | Suppliers FAT test
| PCool-102 | Maximum leakage of helium |  | Measurements
| PCool-103 | Report radiation levels in systems |  | Process control FAT test
| PCool-104 | Purging primary cooling circuit with clean helium |  | Manual testing
| PCool-105 | Pipe support structure |  | Design review
Radiation shielding requirements
(refer to requirement PCool-003)
Internal system requirements (not safety related)
| PCool-150 | Maximum design pressure of the primary cooling circuit |  | Design review
| PCool-151 | Helium maximum inlet temperature |  | Measurements
| PCool-152 | Additional continuous heat removal |  | Measurements
| PCool-153 | Monitoring content of oxygen, carbon and water |  | Measurements
| PCool-154 | Monitoring machine protection data |  | OQ; Operation qualification test
| PCool-155 | Filter operation period |  | Uptime log
| PCool-156 | Filter pressure drop monitoring |  | OQ; Operation qualification test
| PCool-157 | Barrier |  | Design review
| PCool-158 | Pipe design to avoid hot-spots |  | Design review
| PCool-159 | Valve seal type |  | Design review
| PCool-160 | Maximum pressure drop in PCool |  | OQ; Operation qualification test
| PCool-191 | Components life-time |  | Quality assurance from suppliers
| PrC-101 | Max pressure in the PrC buffer tank |  | Measurements
| PrC-102 | Pressure control of PCool |  | OQ; Operation qualification test
| PrC-103 | Pressure control of PrC buffer |  | OQ; Operation qualification test
| PrC-151 | Blower unit capacity in the pressure control system |  | Measurements
| PrC-152 | Purging the pressure control system with clean helium |  | Manual testing
| PrC-153 | Maximum design pressure of the pressure control system |  | Manual testing
| HeRel-101 | Design pressure HeRel |  | Design review
| HeRel-151 | Relief tank capacity | On a filled system both releif valves are opened at the same time | OQ; Operation qualification test
| HeSto-101 | Design pressure Helium storage |  | Design review
| HeSto-151 | Compressor capacity |  | Measurements
| HeSto-152 | Storage tank capacity |  | Design review
| HeSto-153 | Maximum design pressure of gas storage |  | Design review
REQUIREMENTS ON/FROM OTHER SYSTEMS
Physical connections between TSS and PCool
| TSSP-101 | Physical measurement and instrument mounting points for TSS safety classified instruments, e.g. temperatures transmitters or switches |  | Design review
| TSSP-102 | Physical measurement and instrument mounting points for TSS safety classified instruments, flow transmitters or switches |  | Design review
Signal interface and Physical connections between TARGET WHEEL; DRIVE & SHAFT and PCool
| PCool-200 | Order signal variable to PCool to set a fixed cooling power |  | OQ; Operation qualification test
| PCool-201 | Pipe flange with flow to target |  | Design review
| PCool-202 | Pipe flange with flow from target |  | Design review
| PCool-203 | Pipe flange with seal flow to/from target |  | Design review
Requirements imposed on TARGET WHEEL; DRIVE & SHAFT by PCool
| PCool-204 | Maximum amount of particles formed in the target | 3.5 kg during 1 year stated in the TDR | Measurements
| PCool-205 | Max. pressure drop between inlet- and outlet flanges | At max. normal flow | Measurements
Signal interfaces between Process control system and Target Cooling
| N/A | Object signal interfaces; Operational process values, status and command signals | Stated in the appendix to ESS-0019347 ICD-R Target helium cooling – Process control/MPS | Process control FAT test
| MPS-201 | Object signal interfaces; Machine safety process values. A set of machine safety process values defined shall be available for the MPS system. | Stated in the appendix to ESS-0019347 ICD-R Target helium cooling – Process control/MPS. Included signal are marked “MPS:xx”, column "Description" in the appendix to SDD-req. Exactly which signals to be included in this requirement is to be defined by MPS! | Design review
Functional requirements imposed on Process control system by Target Cooling
| PCool-301 | GUI main process picture content for Target cooling |  | Suppliers FAT test
| PCool-302 | GUI detailed process pictures content for all sub systems |  | Suppliers FAT test
| PCool-303 | Pressure control of the primary cooling loop
| PCool-304 | Temperature control of the helium leaving heat exchanger W03
| PCool-305 | Temperature control of the helium leaving heat exchanger W02
| PCool-306 | Temperature control of the return water from heat exchanger W01
| PCool-307 | Perform calculations according to blocks in P&ID's
| PCool-308 | Show process values on process screens
| PCool-309 | Enter and send set points from process screens
| PCool-310 | Send order signals from process screens
| PrC-301 | Pressure control of the buffer tank in the pressure control system
| Heinj-301 | Pressure control of the buffer tank in the Helium Injection system
General process requirements imposed on Target cooling by Target Wheel, drive and shaft
| Wheel-200 | Heat removal power from the target wheel |  | Measurements
| Wheel-201 | Cooling media (Helium) |  | Design review
| Wheel-202 | Cooling media maximum normal flow |  | Measurements
| Wheel-203 | Cooling media temp. values (max. diff. and max. temp. out) |  | Measurements
| Wheel-204 | Maximum operational pressure |  | OQ; Operation qualification test
| Wheel-205 | Minimum operational pressure |  | OQ; Operation qualification test
| Wheel-206 | Pipe connections adapted for plug removal |  | Design review
| Wheel-207 | Seal gas mass flow |  | Measurements
| Wheel-208 | Seal gas maximum temperature |  | Measurements
| Wheel-209 | Cooling media particulates (>= 5 µm) purity |  | Measurements
Requirements imposed on PCool (and Target helium purification) by TARGET WHEEL
| Wheel-801 | Cooling media oxygen maximum concentration |  | Measurements
| Wheel-802 | Cooling media carbon dioxide maximum concentration |  | Measurements
| Wheel-803 | Cooling media water maximum concentration |  | Measurements
| Wheel-804 | Cooling media particulates (< 5 µm) concentration |  | Measurements
| Wheel-805 | Purification system Availability (requirement from the wheel) |  | Uptime log
| Wheel-806 | Purification system capacity at start-up |  | Uptime log
Requirements imposed on Target helium purification by PCool
| PCool-701 | Hydrogen maximum concentration (H2 + HT + T2) |  | Measurements
| PCool-702 | Iodine maximum concentration (I2) |  | Measurements
| PCool-703 | Tritiated water maximum concentration (H2O + HTO + T2O) |  | Measurements
| PCool-704 | Particulates maximum concentration (adsorbed radioactive nuclides) |  | Measurements
| PCool-705 | Total impurity maximum concentration |  | Measurements
| PCool-706 | Purification system Availability (requirement from PCool) |  | Uptime log
| PCool-707 | Purification system capacity after downtime |  | Measurements
| PCool-708 | Operational Temperature range |  | Measurements
| PCool-709 | Operational Pressure range |  | Measurements
| PCool-710 | Operational purification maximum flow |  | Measurements
Requirements imposed on Wheel (and PCool) by Target helium purification
| HePur-201 | Maximum amount of tritium released per time unit |  | Measurements
| HePur-202 | Maximum amount of iodine released per time unit |  | Measurements
| HePur-203 | Particulates max. concentration to avoid clogging of the HEPA filter |  | Measurements
| HePur-204 | Residual air max. concentration (e.g. at start-up or disturbance) |  | Measurements
| HePur-205 | Max. leakage to surroundings (dimensional req. from Helium purification) |  | Measurements
| HePur-206 | Physical connection |  | Design review
Signal interfaces between Intermediate cooling and PCool
| PCool-400 | Target intermediate cooling system status |  | Process control FAT test
| PCool-401 | Temperature in the return water from heat exchanger #1 |  | Measurements
| PCool-402 | Water flow control set point, heat exchanger #1 |  | OQ; Operation qualification test
| PCool-403 | Water flow control set point, heat exchanger #2 |  | OQ; Operation qualification test
| PCool-404 | Water flow control set point, heat exchanger #3 |  | OQ; Operation qualification test
Water flanges interfaces between Intermediate cooling and PCool
| PCool-451 | Pipe flange dimension, material etc. heat exchanger #1 |  | Design review
| PCool-452 | Pipe flange dimension, material etc. heat exchanger #1 |  | Design review
| PCool-453 | Pipe flange dimension, material etc. heat exchanger #2 |  | Design review
| PCool-454 | Pipe flange dimension, material etc. heat exchanger #2 |  | Design review
| PCool-455 | Pipe flange dimension, material etc. heat exchanger #3 |  | Design review
| PCool-456 | Pipe flange dimension, material etc. heat exchanger #3 |  | Design review
| PCool-457 | Transferred normal maximum heat power, heat exchanger #1 |  | Measurements
| PCool-458 | Transferred normal maximum heat power, heat exchanger #2 |  | Measurements
| PCool-459 | Transferred normal maximum heat power, heat exchanger #3 |  | Measurements
Building Interfaces between Target cooling and CF
| PCool-501 | Space requirements room 2, level 110 |  | Design review
| PCool-502 | Space requirements room 4, level 110 |  | Design review
| PCool-503 | Roof hatch size between rooms 2 and 5 |  | Design review
| PCool-504 | Door size, location and orientation rooms 2 & 4, level 110 |  | Design review
| PCool-505 | Door size, location and orientation rooms 2 & 6, level 110 |  | Design review
| PCool-506 | Space requirements room2, level 100 |  | Design review
| PCool-509 | Floor openings for pipes between level 100 and 110 |  | Design review
| PCool-510 | Wall and floor openings for process pipes and electric equipment |  | Design review
Electric power, signal and control system interfaces between Target cooling and CF
| PCool-551 | Electric power; Switchgear total power |  | Design review
| PCool-552 | Electric power; Sockets total power for tools |  | Design review
| PCool-553 | Lighting; total luminosity and allocation |  | Design review
| PCool-554 | Protective earth connections, total number and capacity |  | Design review
| PCool-555 | Back-up power supply capacity for control system parts |  | OQ; Operation qualification test
Interface requirements imposed on HVAC system by Target cooling systems
| PCool-601 | Ventilation capacity during normal operation |  | OQ; Operation qualification test
| PCool-602 | Ventilation capacity and ventilation hoods during maintenance |  | OQ; Operation qualification test
Interface requirements imposed on Radioactive Waste Handling system by Target cooling systems
| PCool-801 | Solid waste dimensions and amounts |  | OQ; Operation qualification test
| PCool-802 | Liquid waste amounts |  | OQ; Operation qualification test
Interface requirements imposed on Fluids supply & process(part of FS) by PrC
| PCool-901 | Nitrogen supply
| PCool-902 | Pristine Helium supply