## Slide 1: TARGET HELIUM COOLING CIRCULATOR REQUIREMENTS & RATIONALE
Jens Harborn
Work unit leader Target cooling
www.europeanspallationsource.se
May 2016

## Slide 2: Outline
Basic process configuration and parameters
Requirements & rationale

## Slide 3: 1. Basic process configuration and parameters Circulator / compressor
    Process parameters for the circulator
Normal operational pressure in the system 10-11 bar(a), i.e. inlet pressure to target rotational seal
Normal flow range 1.2 – 3.0 kg/s, equals 1.0 – 2.4 m3/s
Pressure rise of minimum 1.6 bar, e.g. from 8.4 to 10 bar(a) at mass flow 3.0 kg/s and normal operational temperature
    Pressure drops for the loop is calculated using “FluidFlow 3.3 simulations”, resulting in 0.6 bar
    Pressure drops for the wheel, drive and shaft is calculated using ”Ansys CFX”, resulting in 0.9 bar
    A failure margin of 0.1 bar is added, ”, resulting in total pressure drop of maximum 1.6 bar
Inlet temperature to the circulator 40-60°C
  No particulates of size larger than ≈200-400nm will be in the loop
    Release rate of smallest metallic particulates, formed from direct spallation ejected elements, ≈200-400nm reaches a steady state concentration of 0.40ppm after ≈ 48h of operation. During one year ≈1.2 mg is released from the target tungsten.
    Release rate of largest metallic particulates, eroded, is 10-100g/5400h, equals ≈ 0.1-50 pcs/s with size ≈100µm x ≈50µm x ≈10µm.
    Planned configuration
    Two circulators in parallel
    Each circulator has a flow range of ≈0.6 to ≈1.5 kg/s
    Either the two circulators are operated at the same time or any one of them alone
Notes: Four optional cooling circuit pressures has been considered; 3.6 bar, 7.0 bar, 10 bar and 13 bar. 10 bar was found the optimal based on equipment size, available suppliers for circulator units, general performance and pressure classification considerations.

## Slide 4: 2. Requirements & rationale 1(3) Circulator / compressor
1000-201: Media pure helium. Rationale: N/A.
1000-202: Normal maximum mass flow 3.0 kg/s at normal operational pressure 10-11 bar(g), helium inlet temperature 40°C and total pressure drop in the system 1.6 bar. Rationale: The mass flow is set to this value to give an outlet temperature of max. 240°C when the inlet is 40°C.
1000-204: Maximum operational pressure 11 bar(a) Rationale: The requirement is imposed on system 1010 by target wheel
1000-209: The circulator shall operate in Helium with expected concentration of metallic particulates of 0.40ppm of maximum size 400nm Rationale: Rationale: All parts of the circulator shall be of such high quality that the life-time of the circulator up to 40 years of operation. Current design includes HEPA filters with a bleed flow from/to the loop of 1 g/s. Calculated forming and capturing results in a steady state concentration of 0.40ppm of particulates between 100 and 400nm. All bigger particulates are captured to 100% in the loop filters.
1010-150: Design pressure 13 bar(a). Rationale: normal operational pressure 10 -11 bar(a).
Notes: Four optional cooling circuit pressures has been considered; 3.6 bar, 7.0 bar, 10 bar and 13 bar. 10 bar was found the optimal based on equipment size, available suppliers for circulator units, general performance and pressure classification considerations.

## Slide 5: 2. Requirements & rationale 2(3) Circulator in Target Primary cooling system
1010-001: The target helium cooling system components shall have a reliability according to normal industry standard. Rationale: The reliability for ESS is defined to be the probability of delivering without failure at least 50% of scheduled neutrons over a period of one hour. This means the operation of one circulator out of two is enough to deliver neutrons without failure.
1010-157: The Circulator shall be quality classified according to code RCC-MRx class 3, i.e. essentially following the Pressure Equipment Directive, PED, Norms EN-13445 and EN-13480, and additional requirements listed in RCC-MRx. Rationale: Same requirement is valid for the whole system to fulfil radiation safety requirements.
1010-158: Potential radiological hot-spots in the circulator shall be minimized Rationale: A general requirement for this is defined for the loop in general thus it covers also the circulator. If hot-spots inside the circulator the maintenance procedures will be more complex.
1010-161: Continuously controlled flow within a span of 50-100% of full flow for the total installed circulator function. Thus e.g. 25-100% fulfils this requirement, while 60-100% does not. . Rationale: To save energy and minimize wear, the circuit flow is adapted to actual proton beam power. If a turbo type of circulator, the efficiency is very low at low flows, thus the lower limit depends on the machine type.

## Slide 6: 2. Requirements & rationale 3(3) Circulator in Target Primary cooling system
1010.V001-1: Maximum leakage rate of helium maximum 0.1 g/h from the circulator including pipe joints. Rationale: 10 % of the total allowed leakage for all target helium cooling systems with approximately 50 flange joints in total.
1010.V001-2: Pressure rise of minimum 1.6 bar, defined for 10 bar(a) outlet and 3.0 kg/s and helium inlet temperature 40°C. Rationale: The calculated total pressure drop in the loop + target is 1.5 bar and a margin of 0.1 bar is needed to guarantee enough mass flow in case the final pressure drop is higher than calculated.
1010.V001-3: A condition monitoring system is required Rationale: To keep track of the condition. Preferable integrated in the manufacturer’s proposed stand-alone machine control system.
1010.V001-4: Cooling media maximum amount of oil particulates released 0 g/h. Rationale: Even very small amounts of oil may give a risk of clogging between the tungsten rods in the target wheel.
1010.V001-5: Design temperature 100°C. Rationale: normal operational temperature 40-60°C.
The circulator shall withstand a temperature of 250°C without damage. Rationale: normal operational temperature 40-60°C.
If gas sealed axis the requirements related to this is to be defined together with the supplier since a standard product is preferred to keep the over-all project and technical risk low. For a non-standard solution the development time, cost and risks are higher than for a standard solution.