## Slide 1: CDR Target Helium Circulator Introduction
Ulf Odén
WP2 Manager
www.europeanspallationsource.se
1 June 2016

## Slide 2: Outline
Why a special CDR for the Helium Circulator?
CDR Documents
PDR comments
Safety Classification
Risk and mitigations (EXONAUT)

## Slide 3: CDR for the Helium Circulator
Why a special CDR for the Helium Circulator?
Late contracted In-Kind Partner Start Up of the Final Design Phase postponed >1 year
Helium Circulator Lead Time for delivery on site 24 months (based on early RFI)
To secure the milestone “Installed Target Helium Cooling System” November 2018 procurement of circulator needs to be started up promptly

## Slide 4: CDR Documents
CDR Documents (Target Project Process for Project Phase Transition ESS-0037005)
  SDD Req and Sol
  ICD
  System Verification Plan
  P&ID
  Risk Assessment
  Manufacturing Process Specification and Verification Plan
  Draft of Technical section of Procurement Specifications

## Slide 5: PDR Comments and Follow Up
PDR meeting 4-5 September 2014
PDR committee report ESS-0020169 The main recommendations:
Improve the level of details, especially concerning the interfaces requirements. (ICD’s completed)
Safety classification system, based on a clear methodology applicable at ESS level, (RCC MrX class3)
Increase some design margins (normal operating domain, maximum allowable helium leak during operation…) as this will certainly have a non-negligible effect on operating costs and safety. (SDD Requirements elaborated to include adequate design margins)
PDR Follow Up ESS-0037507 C1 mitigations presented and approved in the CCB meeting April 2016

## Slide 6: PDR Comments (C2) ESS-0020169
The committee recommends that requirements on qualification should be completed.
  The comment is reflecting safety classification. The cooling of the tungsten is not safety classified but the mechanical integrity of the system is assumed to be a safety function. Helium Circulator Confinement is secured for the facility life time.
The committee recommends that lifetime of replaceable components (safety classified) has to be demonstrated.
  Circulator is not safety classified
The committee recommends that operating costs objectives shall be allocated to these systems.
  The circulator will be procured as an “of the shelf component” thus the operating cost will be according to industrial standard.
The committee recommends that, from that allocation, redundancy and class of reliability at component level could be derived and reliability objectives checked.
  The plan is to have two circulators in parallel (2x50%)
The committee recommends that PED regulations shall also be considered for assessing availability of the system (cf. also “classification”).
  RCC MrX class 3, comparison to PED is described in ESS-0037516

## Slide 7: PDR Comments (C2) ESS-0020169
The committee recommends the use of a centralized requirement management at an ESS level (such as DOORS or equivalent system) in order to identify and trace properly the requirements along the design and construction phase.
  Requirements still in SDD Req and ICD documents.
The committee recommends reconsidering sizing of all components (such heat exchangers, filtering concept, piping or pressurizing tanks in PCS), from the updated value of pressure and mass flow in the loop.
  Current documents are reflecting latest operating requirements
The committee recommends that a clear definition of responsibilities between ESS and in-kind partners shall be defined.
  TIK 2.2
The committee recommends that critical milestones of the work plan, especially information coming the dates to freeze the interfaces requirement, are being issued.
  ICD’s approved (except CF)
The committee recommends to review the costs estimates concerning the in kind contribution.
  RFI performed

## Slide 8: Safety Classification
Pipe Rupture the most severe event
Dos to public according to PSAR => 0.32 mSv
Dos limit to public class 3 => < 1 mSv
Dos to workers => 8 mSv
Dos limit to workers class 3 => <20 mSv
The Helium Circulators will be designed according to RCC MRX Class 3. This design requirement is only relevant to the Helium Circulator Casing since the cooling function is not safety classified.
Safety Classification according to “ESS rules for identification and classification….” ESS-0016468

## Slide 9: RISK
ID | Heading | 
36 | Inadequate budget identified for Target Station scope | RFI’s confirms cost estimations
8 | In-kind partners do not deliver full scope or on time | TIK and reference documents specifies the SOW. Secure collaboration and partnership
20 | Difficulty securing in-kind contribution partners causes schedule delays | Late! Early procurement to secure the time schedule
43 | Design and interface information given to CF too late | ICD written but still not approved

## Slide 10
  Final Design
For systems and subsystems within the Target Station the following list of items are typically required for completion of Final Design. Exceptions are to be submitted and approved by the Target Project Manager.
Updated System Design Requirements and Description Documents, including identification of all safety-credited controls (can be separate documents)
Updated Interface Control Documents
Updated System Verification Plan
Updated WBS dictionary that incorporates all project work scope
CAD models, drawings, P&IDs, etc. sufficient to manufacture and/or procure systems, structures, and components
Updated Risk Assessment
Manufacturing Process Specification
Manufacturing Verification Plans
System Analysis Reports
Draft of the technical sections of Procurement Specifications (approval not required at this point)
CDR committee report with responses to recommendations that includes a description of actions completed and submitted for closure in response to recommendations, and a brief action plan for items planned for later closure.
All of these items except the final two, should be approved and submitted to the Critical Design Review committee prior to the CDR. Based on the results of the CDR, all of the above documents should be modified and re-approved, if needed, prior to submittal to the Target Project CCB for approval of Final Design Phase completion. This establishes the Design Baseline.

## Slide 11: RCC MRX N3 – EN 13445 13480
Material
  Low Carbon (IGSCC - 316L OK)
  Max Temp
Load Combination
  Normal Operation Incidents not included in EN 13445
Design
  VT is not enough
  Mitre Elbows >22,5 not allowed