## Slide 1: Presentation of TARGET HELIUM COOLING SYSTEMS May 2016
Jens Harborn
Work unit leader Target cooling
www.europeanspallationsource.se
May 2016

## Slide 2: Outline
Introduction
Purpose and functions
Requirements
Technical solution overview
Technical solution, P&ID’s
Modes of operation
Layout
Classification
Documentation

## Slide 3: 1. INTRODUCTION Target helium cooling systems
ESS Target is a rotating wheel, 2.5m diameter with tungsten rods where the spallation process occurs
The target itself is a small part of the Target station
3MW heat from the spallation process is removed to keep a stable condition
6 m
Target wheel assembly
Proton beam
Tungsten slabs inside

## Slide 4: 1. INTRODUCTION Target helium cooling systems
He
He
Rotary seal
The wheel is connected to the cooling circuit with helium at approximately 1MPa pressure and a flow of 3kg/s
Target cooling consists of 3 systems, the cooling circuit is the main system
The target cooling has 2 support systems; Target Helium Purification and Pristine Helium
The heat is transferred to Target intermediate cooling system

## Slide 5: 2. PURPOSE AND FUNCTIONS Target helium cooling systems
Main functions:
1. Continuous heat removal from the target including pressure control (systems 1010, 1011)
2. Keeping the potentially activated / contaminated fluid enclosed in the system(all)
Sub functions:
3. Collecting potentially radiated particles in a few locations, i.e. filters (system 1010)
4. Maintain particle content in the circuit at an acceptable level (system 1010 and support system 1015)
5. Inject and/or collect helium to the rotational sealing in system Target wheel, shaft, bearings & drive (system 1013)
6. Enable filling, emptying, storage and removal of O2, H2O, CO2 etc (systems 1010, 1011 and support system 1030 Pristine Helium)

## Slide 6: 3. REQUIREMENTS Target helium cooling system
    Selected examples of most important requirements
Continuous heat removal from the target
Operation pressure of the cooling circuit 10-11 bar
Continuous pressure control of the primary circuit
Operation maximum inlet temperature to the Shaft 60°C
Maximum total leakage rate of helium from the total system is 1 g/h
Monitor and report the content of O2, C (Σ carbon compounds) and H2O in the helium gas in the system
The system must be possible to condition to acceptable concentration of helium/nitrogen/air
Guarantee that no particulates larger than 0.5mm enters the target wheel
Notes: Four optional cooling circuit pressures has been considered; 3.6 bar, 7.0 bar, 10 bar and 13 bar. 10 bar was found the optimal based on equipment size, available suppliers for circulator units, general performance and pressure classification considerations.

## Slide 7: 4. TECHNICAL SOLUTION Architecture
Target helium cooling sub systems
1010: Primary cooling circuit
1011: Pressure control & Helium storage
1013: Helium injection
Support systems:
1015 Target He purification
1030 Pristine helium (helium supply)
1140 Offgas system

## Slide 8: 4. TECHNICAL SOLUTION Overview Target cooling

## Slide 9: 5. TECHNICAL SOLUTION P&ID system 1010

## Slide 10: 5. TECHNICAL SOLUTION P&ID system 1011
This system keeps the amount or of helium at a stable level in the loop or to fill/drain

## Slide 11: 5. TECHNICAL SOLUTION P&ID system 1013
This system provide seal flows to rotational sealings of the target

## Slide 12: 6. MODES OF OPERATION Target helium cooling systems
The mode selection is directly dependent on the target station current mode and/or events that for example forces proton beam shut down.
The target helium cooling systems operate together as one system regarding mode of operation.

## Slide 13: 7. LAYOUT Target helium cooling system
  Cooling loop layout

## Slide 14: 8. CLASSIFICATION Overview system 1010
Notes: Four optional cooling circuit pressures has been considered; 3.6 bar, 7.0 bar, 10 bar and 13 bar. 10 bar was found the optimal based on equipment size, available suppliers for circulator units, general performance and pressure classification considerations.

## Slide 15: 8. CLASSIFICATION Target helium cooling system
Proposed classifications:
Primary cooling circuit, system 1010
Class RCCMRX N3(circulator, heat exchangers, filters and valves)
Pressure control & Helium storage, system 1011
PED/EN
Helium injection, system 1013
PED/EN
The loop cooling function, flow & pressure controller functions and the injection functions are not safety classified!

## Slide 16: 9. DOCUMENTATION Target helium cooling systems
Document | State
ESS-0012524 SDD-req; Requirements and references | Ready for approval
ESS-0012527 SDD-sol; System description and functional spec. | Ready for approval
ESS-0040855 PFD Target cooling systems overview | Ready for approval
ESS-0040854 P&ID Target primary cooling, system 1010 | Ready for approval
ESS-0040876 P&ID Pressure control & storage, system 1011 | Ready for approval
ESS-0040855 P&ID Helium seal injection, system 1013 | Ready for approval
ESS-0051819 Manufacture Process specification for Circulator system 1010 | Ready for approval
ESS-0052140 Manufacture Verification plan for Circulator system 1010 | Ready for approval
ESS-0051820 Purchase/procurement specification for the circulator | Approved
ESS-0035383 Target helium cooling system - pressure loss calculation | Ready for approval
.ppt presentation Target Helium Cooling requirements and motivations | N/A
.ppt presentation Target Helium Cooling (this file) | N/A
ESS-0016380 ICD-R Target primary cooling, 1010 – TSS | Approved
ESS-0018673 ICD-R Target primary cooling, 1010 - Target Intermediate cooling, 1046 | Approved
ESS-0019346 ICD Target cooling systems - Target wheel & shaft, 1000 | Approved
ESS-0019347 ICD-R Target cooling systems - Process control system/MPS | Approved
ESS-0030664 ICD-R Target primary cooling, 1010 - Helium purification, 1015 | Approved
ESS-0020682 ICD-R Target cooling systems - CF (site infrastructure & building) | Review
ESS-0038061 ICD-R Target primary cooling pressure control & storage, 1011 - Fluid supply & process | Approved