Accelerator tunnel cooling skids CWS01 & CWS02 functional description

|  | Name | Role/Title |
| --- | --- | --- |
| Owner | Anton Lundmark | Cooling system engineer |
| Reviewer | Akif Coku | WP16 project engineer |
| Reviewer | Piero Valente | Plant and process section coordinator |
| Approver | Anton Lundmark | Cooling system engineer |

| Table of content | Page |
| --- | --- |

1.	<<Heading 1>>	3

1.1.	<<Heading 2>>	3

1.1.1.	<<Heading 3>>	3

2.	Glossary	4

3.	references	4

Document Revision history	4

list of tables

Table 1	Design data for CWL-CWS01	4

Table 2	Design data for CWM-CWS02	4

Table 3	Description of main components	6

list of Figures

Figure 1. Layout of the ESS accelerator. The blue parts indicate the superconducting part of the linac whereas the other colours indicate room temperature elements.	3

Figure 2	Layout of conceptual cooling system	6

# Introduction

The ESS accelerator is a long pulsed superconducting linac that accelerates a 62.5 mA proton beam current to the energy of 2 GeV. Peak beam power to the target will be 125 MW. The layout of the accelerator is shown in Figure 1.

Figure 1. Layout of the ESS accelerator. The blue parts indicate the superconducting part of the linac whereas the other colours indicate room temperature elements.

The accelerator comprise of a number of different subsystems, primarily divided into a warm section (room temperature) and a superconducting section. The last part of the accelerator consists of quadrapole magnets and beam instrumentation that guides the proton beam to the target station (HEBT). The HEBT section may also be used as future upgrade space.

The warm section consists of ion source, Low Energy Beam Transport (LEBT), Radio Frequency Quadrapole (RFQ), Medium Energy Beam Transport (MEBT), and Drift Tube Linac (DTL).

The superconducting section Spokes, Medium Beta, and High Beta. The acceleration in this section is performed via 2 K helium cooled niobium cavitites.

A number of components located in the accelerator tunnel require water-cooling in order to maintain a stable operating temperature.

The cooling of equipment in the tunnel is divided into four separate systems:

- RFQ cooling/tuning system

- DTL cooling/tuning system

- CWL-CWS01 – Cooling system for IS, LEBT, MEBT and DTL Farady cups

- CWM-CWS02 – Cooling system for RF couplers (SPK, MBL, HBL), LWUs (SPK, MBL, HBL), and HEBT/A2T magnets

This system description only concern the CWL-CWS01 and CWM-CWS02. The first part of the naming refers to the conventional facilities cooling systems, CWL (8 °C) and CWM (25 °C) two latter.

# System Data

## Design data

| Table 1 Design data for CWL-CWS01 |  |  |
| --- | --- | --- |
| Parameter | Value | Comment |
| Nominal flow rate | 14.5 m3/h |  |
| Nominal heat load | 85 kW |  |
| Nominal pressure drop | 6 bar | The maximum pressure drop of any load is 5 bar |
| Nominal system volume | TBD |  |
| Design temperature | 50 °C |  |
| Operating temperature range | 15 – 40 °C | Minimum supply temperature to loads - maximum outlet temperature from loads |
| Nominal operating temperature | 20 °C | Operator shall be able to change the set point at least +/- 5 °C. Stability during steady state heat loads shall be better than 1 °C. |
| Primary side water temperature | 8 °C |  |
| Primary side supply pressure | 7 bar(g) |  |
| Primary side maximum allowed pressure drop | 3 bar |  |
| Primary side water quality | Low conductivity water Conductivity: 1 S/cm | Conservative assumption. The 8 °C water may be “clean water” instead of low conductivity. |
| Nominal flow rate | 14.5 m3/h |  |

| Table 2 Design data for CWM-CWS02 |  |  |
| --- | --- | --- |
| Parameter | Value | Comment |
| Nominal flow rate | 85 m3/h |  |
| Nominal heat load | 500 kW |  |
| Nominal pressure drop | 6.5 bar | The maximum pressure drop of the loads is 5 bar |
| Nominal system volume | TBD |  |
| Design temperature | 50 °C |  |
| Operating temperature range | 30 – 45 °C | Minimum supply temperature to loads - maximum outlet temperature from loads |
| Nominal operating temperature | 30 °C | Operator shall be able to change the set point at least +/- 5 °C. Stability during steady state heat loads shall be better than 1 °C. |
| Primary side water temperature | 25 °C |  |
| Primary side supply pressure | 7 bar(g) |  |
| Primary side maximum allowed pressure drop | 3 bar |  |
| Primary side water quality | Low conductivity water Conductivity: 1 S/cm |  |
| Nominal flow rate | 85 m3/h |  |

## Location

The cooling skids are located in G02 level 100, front-end building.

## Applicable standards and norms

- Pressure Equipment Directive (2014/68/EU)

- Low Voltage Directive (2006/95/EC)

- EMC directive (2004/108/EC)

- ISO and EU standards; primarily EN 13480, EN 60204 and its normative references

# Control & Monitoring

Component references are according to Figure 1.

Figure 2	Layout of conceptual cooling system

| Table 3 Description of main components |  |
| --- | --- |
| Component | Purpose |
| FIT010 | Measure full flow |
| QT011 | Conductivity meter |
| TIT005 | Measure temperature of return flow |
| PIT004/PIT005 | Differential pressure measurement for control of pump |
| TIT001/TIT002 | Primary side temperatures |
| FIT000 | Primary flow |
| V022 | Main temperature control valve |
| V025 | Bypass control valve (in case of low heat load) |
| V010/V011 | Non-return valves |

## Main functionality

Both CWS01 and CWS02 have the same control layout, they only differ in supply temperature and cooling capacity.

The primary purpose of the cooling system is to deliver cooled low conductivity water to the components in the tunnel. The system is equipped with a degassing unit in order to maintain low oxygen content, which inhibits corrosion (primarily copper corrosion).

The cooling system is equipped with frequency driven pumps, which controls the differential pressure.

The pumps automatically interchange from operation to cold stand-by monthly. The switching operation is controlled not to disrupt cooling to loads.

It is possible to operate the pumps manually, i.e. the PLC has a manual control mode.

In case of pump failure (motor protection trip) or erroneous flow control, the stand-by pump will start automatically and the other is stopped.

In case of low heat load the control system can make use of a bypass line, see V025 in Figure 1.

## Degassing, filtering and deionization

The cooling skids are equipped with the following water treatment features:

- Deionization unit, capable of maintaining a conductivity of at least 0.1 μS/cm

- Degassing system, able to maintain oxygen content < 15 ppb

- Filtering unit, 100 μm, operating with a bypass flow of up to 10% of the nominal flow

## Trips and alarms

The cooling skids have the following alarms and interlocks.

Alarms:

- PLC error

- high conductivity

- high temp

- low flow

- low pressure in exp vessel

- pump error

- control valve error

- instrument error

- filter replacement

Trips:

- high high temperature

- low flow for sustained time

- low low level in exp tank

- high high conductivity

- PLC error

# Glossary

| Term | Definition |
| --- | --- |
| CWL | Cooling Water Low, 8 °C |
| CWM | Cooling Water Medium, 25 °C |
| CWS | Cooling Water System |
| LEBT | Low Energy Beam Transport |
| MEBT | Medium Energy Beam Transport |
| HEBT | High Energy Beam Transport |
| A2T | Accelerator to Target (last part of accelerator before target station) |

# references

- -

Document Revision history

| Revision | Reason for and description of change | Author | Date |
| --- | --- | --- | --- |
| 1 | First issue | Anton Lundmark | 2016-10-11 |